## Import Data
Sub Station | Serial Number | Date of Test | Testing Kit Used | HV Voltage | LV Voltage | Tertiary Voltage | Test Voltage | Ambient Temperature | Oil Temperature | Overall Result | Observation | Recommendation
sub_station | serial_number | test_date | test_kit | hv_voltage_kv | lv_voltage_kv | tv_voltage_kv | test_voltage_v | ambient_temp_c | oil_temp_c | overall_result | observation | recommendation
Name of substation / location | Equipment serial number (used to match equipment) | YYYY-MM-DD format | Test Conditions | kV | kV | kV | V | °C | °C | Overall Assessment | Overall Assessment | Overall Assessment
220kV BIAL SS | HT-1690/12569 | 2026-02-15 | Megger IDAX 350 | 230 | 110 | 11 | 140 | 32 | 41 | PASS | Tan delta curve within expected envelope across full frequency sweep. Estimated moisture ~1.8% — dry insulation. | No action required. Repeat DFR at next scheduled maintenance interval.

## DFR Measurements
Measurement Mode | Frequency (Hz) | Capacitance (pF) | Tan Delta (%)
measurement_mode | frequency_hz | capacitance_pf | tan_delta_percent | __table_key__=dfr_measurements
GST | 0.001 | 9728 | 0.4443
GST | 0.002 | 9716.6 | 0.4186
GST | 0.005 | 9701.4 | 0.3881
GST | 0.01 | 9690 | 0.3675
GST | 0.02 | 9678.6 | 0.3491
GST | 0.05 | 9663.4 | 0.328
GST | 0.1 | 9652 | 0.3147
GST | 0.2 | 9640.6 | 0.3035
GST | 0.5 | 9625.4 | 0.292
GST | 1 | 9614 | 0.2859
GST | 2 | 9602.6 | 0.2819
GST | 5 | 9587.4 | 0.28
GST | 10 | 9576 | 0.2811
GST | 20 | 9564.6 | 0.2843
GST | 50 | 9549.4 | 0.292
GST | 100 | 9538 | 0.3003
GST | 200 | 9526.6 | 0.3108
GST | 500 | 9511.4 | 0.328
GST | 1000 | 9500 | 0.3435
UST | 0.001 | 5293.6 | 0.3643
UST | 0.002 | 5288.9 | 0.3433
UST | 0.005 | 5282.7 | 0.3182
UST | 0.01 | 5278 | 0.3013
UST | 0.02 | 5273.3 | 0.2862
UST | 0.05 | 5267.1 | 0.269
UST | 0.1 | 5262.4 | 0.258
UST | 0.2 | 5257.7 | 0.2489
UST | 0.5 | 5251.5 | 0.2395
UST | 1 | 5246.8 | 0.2344
UST | 2 | 5242.1 | 0.2312
UST | 5 | 5235.9 | 0.2296
UST | 10 | 5231.2 | 0.2305
UST | 20 | 5226.5 | 0.2332
UST | 50 | 5220.3 | 0.2394
UST | 100 | 5215.6 | 0.2462
UST | 200 | 5210.9 | 0.2548
UST | 500 | 5204.7 | 0.2689
UST | 1000 | 5200 | 0.2817