## Import Data
Sub Station | Serial Number | Date of Test | Testing Kit Used | HV Voltage | LV Voltage | Tertiary Voltage | Test Voltage | Ambient Temperature | Oil Temperature | Overall Result | Observation | Recommendation
sub_station | serial_number | test_date | test_kit | hv_voltage_kv | lv_voltage_kv | tv_voltage_kv | test_voltage_v | ambient_temp_c | oil_temp_c | overall_result | observation | recommendation
Name of substation / location | Equipment serial number (used to match equipment) | YYYY-MM-DD format | Test Conditions | kV | kV | kV | V | °C | °C | Overall Assessment | Overall Assessment | Overall Assessment
220kV BIAL SS | HT-1690/12569 | 2026-08-25 | Megger IDAX 350 | 230 | 110 | 11 | 140 | 32 | 41 | FAIL | Tan delta rises sharply at low frequency, exceeding the critical limit — indicates elevated moisture in the paper insulation. | Tan delta above acceptable limit — investigate insulation moisture/aging; consider oil reconditioning or drying.

## DFR Measurements
Measurement Mode | Frequency (Hz) | Capacitance (pF) | Tan Delta (%)
measurement_mode | frequency_hz | capacitance_pf | tan_delta_percent | __table_key__=dfr_measurements
GST | 0.001 | 9728 | 1.7859
GST | 0.002 | 9716.6 | 1.5508
GST | 0.005 | 9701.4 | 1.2707
GST | 0.01 | 9690 | 1.0819
GST | 0.02 | 9678.6 | 0.9131
GST | 0.05 | 9663.4 | 0.7205
GST | 0.1 | 9652 | 0.5979
GST | 0.2 | 9640.6 | 0.4953
GST | 0.5 | 9625.4 | 0.3902
GST | 1 | 9614 | 0.3339
GST | 2 | 9602.6 | 0.2975
GST | 5 | 9587.4 | 0.28
GST | 10 | 9576 | 0.2899
GST | 20 | 9564.6 | 0.3197
GST | 50 | 9549.4 | 0.3898
GST | 100 | 9538 | 0.4659
GST | 200 | 9526.6 | 0.562
GST | 500 | 9511.4 | 0.7195
GST | 1000 | 9500 | 0.8619
UST | 0.001 | 5293.6 | 1.4644
UST | 0.002 | 5288.9 | 1.2717
UST | 0.005 | 5282.7 | 1.042
UST | 0.01 | 5278 | 0.8872
UST | 0.02 | 5273.3 | 0.7487
UST | 0.05 | 5267.1 | 0.5908
UST | 0.1 | 5262.4 | 0.4903
UST | 0.2 | 5257.7 | 0.4061
UST | 0.5 | 5251.5 | 0.32
UST | 1 | 5246.8 | 0.2738
UST | 2 | 5242.1 | 0.244
UST | 5 | 5235.9 | 0.2296
UST | 10 | 5231.2 | 0.2377
UST | 20 | 5226.5 | 0.2622
UST | 50 | 5220.3 | 0.3196
UST | 100 | 5215.6 | 0.382
UST | 200 | 5210.9 | 0.4608
UST | 500 | 5204.7 | 0.59
UST | 1000 | 5200 | 0.7068