## Import Data
Sub Station | Serial Number | Date of Test | Testing Kit Used | Sweep Frequency Range | No. of Measurement Points | Tap Position | Ambient Temperature | Oil Temperature | Overall Result | Suspected Fault Type | Observation | Recommendation
sub_station | serial_number | test_date | test_kit | sweep_range | measurement_points | tap_position | ambient_temp_c | oil_temp_c | overall_result | fault_type | observation | recommendation
Name of substation / location | Equipment serial number (used to match equipment) | YYYY-MM-DD format | Test Conditions | Test Conditions | Test Conditions | Test Conditions | °C | °C | Overall Assessment | Overall Assessment | Overall Assessment | Overall Assessment
220kV BIAL SS | HT-1690/12569 | 2026-08-25 | Omicron FRAnalyzer | 20 Hz - 2 MHz | 30 | 9 (Nominal) | 32 | 41 | FAIL | Winding Deformation | HV-N winding correlation dropped sharply below the acceptance floor across all frequency bands — trace shape differs from the reference sweep, suggesting possible winding deformation. | SFRA correlation below acceptance floor — investigate winding/core mechanical integrity before energising.

## SFRA Measurements (Amplitude vs
Winding / Connection | Frequency (Hz) | Amplitude (dB) | Phase (°)
winding | frequency_hz | amplitude_db | phase_deg | __table_key__=sfra_measurements
HV-N | 20 | -21.19 | 57.8
HV-N | 29.7 | -19.81 | 59.7
HV-N | 44.2 | -18.43 | 59.8
HV-N | 65.8 | -17.05 | 58.2
HV-N | 97.9 | -15.67 | 54.8
HV-N | 145.6 | -14.3 | 49.8
HV-N | 216.5 | -12.92 | 43.3
HV-N | 322.1 | -11.55 | 35.5
HV-N | 479 | -12 | 26.7
HV-N | 712.4 | -28.16 | 17.1
HV-N | 1059.7 | -17.84 | 7
HV-N | 1576.1 | -6.31 | -3.4
HV-N | 2344.2 | -7.36 | -13.6
HV-N | 3486.7 | -8.74 | -23.4
HV-N | 5185.9 | -10.12 | -32.5
HV-N | 7713.2 | -11.5 | -40.7
HV-N | 11472.3 | -12.88 | -47.7
HV-N | 17063.4 | -14.26 | -53.2
HV-N | 25379.2 | -15.64 | -57.2
HV-N | 37747.8 | -17.02 | -59.5
HV-N | 56144.3 | -18.39 | -60
HV-N | 83506.4 | -19.77 | -58.7
HV-N | 124203.4 | -21.15 | -55.7
HV-N | 184734.2 | -22.01 | -51
HV-N | 274764.8 | -14.84 | -44.8
HV-N | 408671.9 | -22.28 | -37.3
HV-N | 607839.1 | -26.65 | -28.7
HV-N | 904070.7 | -28.05 | -19.3
HV-N | 1344671.5 | -29.43 | -9.2
HV-N | 2000000 | -30.81 | 1.1
LV-N | 20 | -19.19 | 57.8
LV-N | 29.7 | -17.81 | 59.7
LV-N | 44.2 | -16.43 | 59.8
LV-N | 65.8 | -15.05 | 58.2
LV-N | 97.9 | -13.67 | 54.8
LV-N | 145.6 | -12.3 | 49.8
LV-N | 216.5 | -10.92 | 43.3
LV-N | 322.1 | -9.54 | 35.5
LV-N | 479 | -8.16 | 26.7
LV-N | 712.4 | -6.78 | 17.1
LV-N | 1059.7 | -5.8 | 7
LV-N | 1576.1 | -14.56 | -3.4
LV-N | 2344.2 | -19.55 | -13.6
LV-N | 3486.7 | -7.72 | -23.4
LV-N | 5185.9 | -8.12 | -32.5
LV-N | 7713.2 | -9.5 | -40.7
LV-N | 11472.3 | -10.88 | -47.7
LV-N | 17063.4 | -12.26 | -53.2
LV-N | 25379.2 | -13.64 | -57.2
LV-N | 37747.8 | -15.02 | -59.5
LV-N | 56144.3 | -16.39 | -60
LV-N | 83506.4 | -17.77 | -58.7
LV-N | 124203.4 | -19.15 | -55.7
LV-N | 184734.2 | -20.53 | -51
LV-N | 274764.8 | -21.82 | -44.8
LV-N | 408671.9 | -18.49 | -37.3
LV-N | 607839.1 | -19.72 | -28.7
LV-N | 904070.7 | -25.95 | -19.3
LV-N | 1344671.5 | -27.43 | -9.2
LV-N | 2000000 | -28.81 | 1.1
TV-N | 20 | -23.19 | 57.8
TV-N | 29.7 | -21.81 | 59.7
TV-N | 44.2 | -20.43 | 59.8
TV-N | 65.8 | -19.05 | 58.2
TV-N | 97.9 | -17.67 | 54.8
TV-N | 145.6 | -16.3 | 49.8
TV-N | 216.5 | -14.92 | 43.3
TV-N | 322.1 | -13.54 | 35.5
TV-N | 479 | -12.16 | 26.7
TV-N | 712.4 | -10.78 | 17.1
TV-N | 1059.7 | -9.4 | 7
TV-N | 1576.1 | -8.02 | -3.4
TV-N | 2344.2 | -9.43 | -13.6
TV-N | 3486.7 | -15.14 | -23.4
TV-N | 5185.9 | -26.93 | -32.5
TV-N | 7713.2 | -16.05 | -40.7
TV-N | 11472.3 | -14.9 | -47.7
TV-N | 17063.4 | -16.26 | -53.2
TV-N | 25379.2 | -17.64 | -57.2
TV-N | 37747.8 | -19.02 | -59.5
TV-N | 56144.3 | -20.39 | -60
TV-N | 83506.4 | -21.77 | -58.7
TV-N | 124203.4 | -23.15 | -55.7
TV-N | 184734.2 | -24.53 | -51
TV-N | 274764.8 | -25.91 | -44.8
TV-N | 408671.9 | -27.13 | -37.3
TV-N | 607839.1 | -24 | -28.7
TV-N | 904070.7 | -27.41 | -19.3
TV-N | 1344671.5 | -31.4 | -9.2
TV-N | 2000000 | -32.81 | 1.1

## Per-Winding Correlation
Winding | CC — LF (1k–100kHz) | CC — MF (100k–600kHz) | CC — HF (600k–1MHz) | Assessment
winding | cc_lf | cc_mf | cc_hf | assessment | __table_key__=correlation_analysis
HV-N | 0.9 | 0.88 | 0.85 | Abnormal
LV-N | 0.998 | 0.993 | 0.982 | Normal
TV-N | 0.997 | 0.991 | 0.979 | Normal
HV-LV | 0.996 | 0.99 | 0.975 | Normal
HV-TV | 0.995 | 0.989 | 0.973 | Normal
LV-TV | 0.994 | 0.988 | 0.971 | Normal