## Import Data
Sub Station | Serial Number | Date of Test | Testing Kit Used | Sweep Frequency Range | No. of Measurement Points | Tap Position | Ambient Temperature | Oil Temperature | Overall Result | Suspected Fault Type | Observation | Recommendation
sub_station | serial_number | test_date | test_kit | sweep_range | measurement_points | tap_position | ambient_temp_c | oil_temp_c | overall_result | fault_type | observation | recommendation
Name of substation / location | Equipment serial number (used to match equipment) | YYYY-MM-DD format | Test Conditions | Test Conditions | Test Conditions | Test Conditions | °C | °C | Overall Assessment | Overall Assessment | Overall Assessment | Overall Assessment
220kV BIAL SS | HT-1690/12570 | 2026-02-15 | Omicron FRAnalyzer | 20 Hz - 2 MHz | 30 | 9 (Nominal) | 31 | 39 | PASS | None | All winding traces overlay well with previous routine measurement and with sister unit TR-1. No resonance shifts observed. | Retain traces as reference for next comparison.

## SFRA Measurements (Amplitude vs
Winding / Connection | Frequency (Hz) | Amplitude (dB) | Phase (°)
winding | frequency_hz | amplitude_db | phase_deg | __table_key__=sfra_measurements
HV-N | 20 | -21.69 | 55.9
HV-N | 29.7 | -20.31 | 57.7
HV-N | 44.2 | -18.93 | 57.8
HV-N | 65.8 | -17.55 | 56.2
HV-N | 97.9 | -16.17 | 53
HV-N | 145.6 | -14.8 | 48.1
HV-N | 216.5 | -13.42 | 41.9
HV-N | 322.1 | -12.04 | 34.3
HV-N | 479 | -11.56 | 25.8
HV-N | 712.4 | -24.19 | 16.5
HV-N | 1059.7 | -20.54 | 6.7
HV-N | 1576.1 | -7.07 | -3.2
HV-N | 2344.2 | -7.86 | -13.1
HV-N | 3486.7 | -9.24 | -22.6
HV-N | 5185.9 | -10.62 | -31.5
HV-N | 7713.2 | -12 | -39.3
HV-N | 11472.3 | -13.38 | -46.1
HV-N | 17063.4 | -14.76 | -51.4
HV-N | 25379.2 | -16.14 | -55.3
HV-N | 37747.8 | -17.52 | -57.5
HV-N | 56144.3 | -18.89 | -58
HV-N | 83506.4 | -20.27 | -56.7
HV-N | 124203.4 | -21.65 | -53.8
HV-N | 184734.2 | -22.72 | -49.3
HV-N | 274764.8 | -16.92 | -43.4
HV-N | 408671.9 | -22.35 | -36.1
HV-N | 607839.1 | -27.14 | -27.8
HV-N | 904070.7 | -28.55 | -18.6
HV-N | 1344671.5 | -29.93 | -8.9
HV-N | 2000000 | -31.31 | 1
LV-N | 20 | -19.69 | 55.9
LV-N | 29.7 | -18.31 | 57.7
LV-N | 44.2 | -16.93 | 57.8
LV-N | 65.8 | -15.55 | 56.2
LV-N | 97.9 | -14.17 | 53
LV-N | 145.6 | -12.8 | 48.1
LV-N | 216.5 | -11.42 | 41.9
LV-N | 322.1 | -10.04 | 34.3
LV-N | 479 | -8.66 | 25.8
LV-N | 712.4 | -7.28 | 16.5
LV-N | 1059.7 | -6.09 | 6.7
LV-N | 1576.1 | -11.88 | -3.2
LV-N | 2344.2 | -20.13 | -13.1
LV-N | 3486.7 | -8.66 | -22.6
LV-N | 5185.9 | -8.63 | -31.5
LV-N | 7713.2 | -10 | -39.3
LV-N | 11472.3 | -11.38 | -46.1
LV-N | 17063.4 | -12.76 | -51.4
LV-N | 25379.2 | -14.14 | -55.3
LV-N | 37747.8 | -15.52 | -57.5
LV-N | 56144.3 | -16.89 | -58
LV-N | 83506.4 | -18.27 | -56.7
LV-N | 124203.4 | -19.65 | -53.8
LV-N | 184734.2 | -21.03 | -49.3
LV-N | 274764.8 | -22.35 | -43.4
LV-N | 408671.9 | -20.01 | -36.1
LV-N | 607839.1 | -20.42 | -27.8
LV-N | 904070.7 | -26.44 | -18.6
LV-N | 1344671.5 | -27.93 | -8.9
LV-N | 2000000 | -29.31 | 1
TV-N | 20 | -23.69 | 55.9
TV-N | 29.7 | -22.31 | 57.7
TV-N | 44.2 | -20.93 | 57.8
TV-N | 65.8 | -19.55 | 56.2
TV-N | 97.9 | -18.17 | 53
TV-N | 145.6 | -16.8 | 48.1
TV-N | 216.5 | -15.42 | 41.9
TV-N | 322.1 | -14.04 | 34.3
TV-N | 479 | -12.66 | 25.8
TV-N | 712.4 | -11.28 | 16.5
TV-N | 1059.7 | -9.9 | 6.7
TV-N | 1576.1 | -8.52 | -3.2
TV-N | 2344.2 | -9.89 | -13.1
TV-N | 3486.7 | -14.12 | -22.6
TV-N | 5185.9 | -25.62 | -31.5
TV-N | 7713.2 | -17 | -39.3
TV-N | 11472.3 | -15.41 | -46.1
TV-N | 17063.4 | -16.76 | -51.4
TV-N | 25379.2 | -18.14 | -55.3
TV-N | 37747.8 | -19.52 | -57.5
TV-N | 56144.3 | -20.89 | -58
TV-N | 83506.4 | -22.27 | -56.7
TV-N | 124203.4 | -23.65 | -53.8
TV-N | 184734.2 | -25.03 | -49.3
TV-N | 274764.8 | -26.41 | -43.4
TV-N | 408671.9 | -27.63 | -36.1
TV-N | 607839.1 | -25.09 | -27.8
TV-N | 904070.7 | -28.55 | -18.6
TV-N | 1344671.5 | -31.91 | -8.9
TV-N | 2000000 | -33.31 | 1

## Per-Winding Correlation
Winding | CC — LF (1k–100kHz) | CC — MF (100k–600kHz) | CC — HF (600k–1MHz) | Assessment
winding | cc_lf | cc_mf | cc_hf | assessment | __table_key__=correlation_analysis
HV-N | 0.999 | 0.996 | 0.99 | Normal
LV-N | 0.998 | 0.994 | 0.984 | Normal
TV-N | 0.997 | 0.992 | 0.981 | Normal
HV-LV | 0.997 | 0.991 | 0.977 | Normal
HV-TV | 0.996 | 0.99 | 0.975 | Normal
LV-TV | 0.995 | 0.989 | 0.973 | Normal