## Import Data
Sub Station | Serial Number | Date of Test | Testing Kit Used | HV Voltage | LV Voltage | Tertiary Voltage | Test Voltage | Ambient Temperature | Oil Temperature | Overall Result | Observation | Recommendation
sub_station | serial_number | test_date | test_kit | hv_voltage_kv | lv_voltage_kv | tv_voltage_kv | test_voltage_v | ambient_temp_c | oil_temp_c | overall_result | observation | recommendation
Name of substation / location | Equipment serial number (used to match equipment) | YYYY-MM-DD format | Test Conditions | kV | kV | kV | V | °C | °C | Overall Assessment | Overall Assessment | Overall Assessment
220kV BIAL SS | HT-1690/12570 | 2026-02-15 | Megger IDAX 350 | 230 | 110 | 11 | 140 | 31 | 39 | PASS | Tan delta curve within expected envelope, slightly better than sister unit TR-1. Estimated moisture ~1.4% — dry insulation. | No action required. Repeat DFR at next scheduled maintenance interval.

## DFR Measurements
Measurement Mode | Frequency (Hz) | Capacitance (pF) | Tan Delta (%)
measurement_mode | frequency_hz | capacitance_pf | tan_delta_percent | __table_key__=dfr_measurements
GST | 0.001 | 9574.4 | 0.3721
GST | 0.002 | 9563.1 | 0.3495
GST | 0.005 | 9548.3 | 0.3225
GST | 0.01 | 9537 | 0.3041
GST | 0.02 | 9525.7 | 0.2875
GST | 0.05 | 9510.9 | 0.2684
GST | 0.1 | 9499.6 | 0.2561
GST | 0.2 | 9488.3 | 0.2456
GST | 0.5 | 9473.5 | 0.2344
GST | 1 | 9462.2 | 0.2281
GST | 2 | 9450.9 | 0.2236
GST | 5 | 9436.1 | 0.2204
GST | 10 | 9424.8 | 0.2201
GST | 20 | 9413.5 | 0.2216
GST | 50 | 9398.7 | 0.2264
GST | 100 | 9387.4 | 0.2321
GST | 200 | 9376.1 | 0.2396
GST | 500 | 9361.3 | 0.2524
GST | 1000 | 9350 | 0.2641
UST | 0.001 | 5191.8 | 0.2977
UST | 0.002 | 5187.2 | 0.2796
UST | 0.005 | 5181.1 | 0.258
UST | 0.01 | 5176.5 | 0.2433
UST | 0.02 | 5171.9 | 0.23
UST | 0.05 | 5165.8 | 0.2148
UST | 0.1 | 5161.2 | 0.2049
UST | 0.2 | 5156.6 | 0.1965
UST | 0.5 | 5150.5 | 0.1875
UST | 1 | 5145.9 | 0.1825
UST | 2 | 5141.3 | 0.1789
UST | 5 | 5135.2 | 0.1763
UST | 10 | 5130.6 | 0.1761
UST | 20 | 5126 | 0.1773
UST | 50 | 5119.9 | 0.1811
UST | 100 | 5115.3 | 0.1857
UST | 200 | 5110.7 | 0.1917
UST | 500 | 5104.6 | 0.2019
UST | 1000 | 5100 | 0.2113