## 220 KV BEGUR
Name Of Station : Begur(International Airport) |  | Capacity : 20MVA |  |  | Serial Number : SO-0000386 |  |  |  |  | Name Of Station : Begur(International Airport) |  | Capacity : 20MVA |  | Serial Number : PT-7758 |  |  |  | Name Of Station : Begur(International Airport) |  | Capacity : 100MVA |  | Serial Number : KT-100000/51 | Name Of Station : Begur(International Airport) |  | Capacity : 100MVA |  |  | Serial Number : HT-1690/12570 | [14 empty] | Name Of Station : Begur(International Airport) |  | Capacity : 100MVA |  |  | Serial Number : HT-1690/12569
SSMD : BIAL |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 23-Dec-16 |  |  |  |  | SSMD : BIAL |  | Voltage Class : 66/11 KV |  | Date Of Commission : 30-Jun-17 |  |  |  | SSMD : BIAL |  | Voltage Class : 220/66/11 KV |  | Date Of Commission : | SSMD : BIAL |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 17-Jul-07 | [14 empty] | SSMD : BIAL |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 26-Jan-07
Zone : BANGALORE |  | Make : TAL |  |  | YOM : 2016 |  |  |  |  | Zone : BANGALORE |  | Make : IMP |  | YOM : 2017 |  |  |  | Zone : BANGALORE |  | Make : KANIHAR |  | YOM : 2021 | Zone : BANGALORE |  | Make : EMCO |  |  | YOM : 2006 | [14 empty] | Zone : BANGALORE |  | Make : EMCO |  |  | YOM : 2006
[5 empty] | Permissible limits as per 1866-2017 | [5 empty] | Permissible limits as per IS 1866:2000 |  | Permissible limits as per 1866-2017 | [5 empty] | Permissible limits as per 1866-2017 |  |  |  |  | Permissible limits as per IS 1866:2000 | [13 empty] | Permissible limits as per 1866-2017 | [5 empty] | Permissible limits as per IS 1866:2000 | [12 empty] | Permissible limits as per 1866-2017
Last Filtn. Date |  | 2016 | 2016 | 2016 |  | 2016 | 2016 | 2016 | 2016 | Last Filtn. Date |  | 2017 |  | 2017 | 2017 | 2017 | 2017 | Last Filtn. Date |  |  | 2022 | 2022 | Last Filtn. Date |  | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 |  | 2007 |  | 2007 | 2007 | 2007 | 2007 | Last Filtn. Date |  | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 |  | 2007 | 2007 | 2007 | 2007
Sampling Date | [9 empty] | Sampling Date | [7 empty] | Sampling Date |  |  |  |  | Sampling Date | [19 empty] | Sampling Date
Date of Test |  | 2017-05-04 | 2017-08-05 | 2020-07-17 | Vol Class Good Fair Poor | 2021-08-23 | 2022-11-30 | 2023-12-18 | 2025-02-20 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-07-17 | Vol Class Good Fair Poor | 2021-08-23 | 2022-11-30 | 2023-12-18 | 2025-02-21 | Date of Test | Vol Class Good Fair Poor |  | 2023-12-07 | 2025-03-21 | Date of Test | Permissible limits as per IS 1866:2000 | 2008-05-31 | 2009-05-20 | 2010-05-24 | 2011-05-02 | 2012-04-20 | 2013-05-24 | 2014-05-15 | 2015-08-12 | 2015-11-02 | 2017-05-04 | 2017-08-05 | 2019-10-14 | 2020-07-17 | Vol Class Good Fair Poor | 2021-08-23 | 2022-10-18 | 2023-12-07 | 2025-03-21 | Date of Test | Permissible limits as per IS 1866:2000 | 2008-06-03 | 2009-05-21 | 2010-05-24 | 2011-05-02 | 2012-04-20 | 2013-05-24 | 2014-05-15 | 2015-08-12 | 2015-11-02 | 2017-05-04 | 2017-08-05 | 2020-07-17 | Vol Class Good Fair Poor | 2021-08-23 | 2022-10-18 | 2023-12-07 | 2025-03-21
Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.0034 | 0.0085 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0095 | 0.0129 | 0.0151 | 0.008 | Aci dity | 0.3 mg KOH / gm(Max) | 0.01 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0071 | 0.0134 | 0.0143 | 0.0174 | Aci dity | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 |  | 0.0099 | 0 | Aci dity | 0.3 mg KOH / gm(Max) | 0.007 | 0.013 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0109 | 0.0198 | 0.0072 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0088 | 0.0076 | 0.0192 | 0.0113 | Aci dity | 0.3 mg KOH / gm(Max) | 0.005 | 0.013 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0114 | 0.0077 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0085 | 0.0083 | 0.0136 | 0.012
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 87.96 | 185.2 | 186.3 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1600 | 1900 | 1614 | 1946.8 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 113.6 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1026 | 620 | 860 | 870 | Resis tivity | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 |  | 1270 | 576 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 228 | 48.7 | 50.1 | 50.9 | 50.9 | 90.9 | 85.9 | 97.42 | 77.37 | 148.9 | 114.9 | 73.75 | 121.32 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 870 | 544 | 780 | 576 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 69.9 | 66.1 | 62.4 | 60.9 | 61.6 | 61.9 | 61.4 | 60.26 | 187.97 | 132.7 | 204.4 | 176.8 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1638 | 1300 | 1060 | 914
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00051 | 0.0002 | 0.00051 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00047 | 0.000755 | 0.00066 | 0.00089 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00056 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.0009 | 0.001989 | 0.00211 | 0.001882 | Tan - Delta | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  | 0.001373 | 0.0024 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0007 | 0.0003 | 0.0006 | 0.0008 | 0.0009 | 0.005 | 0.0012 | 0.00094 | 0.00019 | 0.00018 | 0.00045 | 0.00134 | 0.000166 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.0006 | 0.0017 | 0.000635 | 0.0024 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0021 | 0.0005 | 0.0009 | 0.0009 | 0.0008 | 0.0009 | 0.0012 | 0.0015 | 0.00034 | 0.00016 | 0.0001 | 0.00053 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.0019 | 0.00062 | 0.00148 | 0.00151
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  |  |  |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  |  |  |  | BDV (T) | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 70 | 74 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 2008-05-31: 66; 2009-05-20: 74; 2011-05-02: 71; 2012-04-20: 76; 2017-05-04: 89 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  |  |  | 74 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 60 | 70 |  | 84 | 76 | 76 |  |  |  | 80 |  |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30
BDV (B) |  | 62 | 69 | 61 |  | 70 | 41 | 40 | 64 | BDV (B) |  | 55 |  | 71 | 78 | 65 | 70 | BDV (B) |  |  | 47 | 71 | BDV (B) |  | 63 | 63 | 63 | 52 | 68 | 76 | 73 | 56 | 82 | 85 | 65 | 57 | 65 |  | 72 | 68 | 46 | 71 | BDV (B) |  | 57 | 69 | 58 | 64 | 70 | 74 | 78 | 52 | 87 | 56 | 56 | 78 |  | 62 | 72 | 52 | 77
IFT | 15 Dynes / cm (Min) | 40.01 | 42.19 | 38.35 | >25 20-25 <20 (for all voltage class) | 36.78 | 32.51 | 35.81 | 38.31 | IFT | 15 Dynes / cm (Min) | 40.45 | >25 20-25 <20 (for all voltage class) | 35.1 | 36.12 | 36.17 | 37.68 | IFT | >25 20-25 <20 (for all voltage class) |  | 37.64 | 34.87 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40.8 | 38.74 | 34.66 | 38.29 | >25 20-25 <20 (for all voltage class) | 32.56 | 33.88 | 33.72 | 34.87 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41.79 | 34.83 | 33.76 | >25 20-25 <20 (for all voltage class) | 36.6 | 32.98 | 32.17 | 36.61
F P | 125° C (Min) | 168 | 158 | 169 | Max decrease 10% (for all class of Voltage) | 167 | 169 | 170 | 159 | F P | 125° C (Min) | 156 | Max decrease 10% (for all class of Voltage) | 160 | 156 | 163 | 163 | F P | Max decrease 10% (for all class of Voltage) |  | 160 | 165 | F P | 125° C (Min) | 157 | 153 | 153 | 159 | 159 | 157 | 157 | 156 | 156 | 172 | 155 | 164 | 168 | Max decrease 10% (for all class of Voltage) | 162 | 165 | 166 | 165 | F P | 125° C (Min) |  | 153 | 151 | 157 | 157 | 156 | 156 | 155 | 156 | 166 | 158 | 172 | Max decrease 10% (for all class of Voltage) | 163 | 160 | 164 | 159
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 11 | 9 | 7 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 4 | 32 | 22 | 12 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 5 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 2 | 10 | 16 | 10 | ppm | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 |  | 25 | 16 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 11 | 5 | 8 | 20 | 6 | 4 | 7 | 16 | 12 | 8 | 8 | 18 | 4 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 4 | 14 | 17 | 16 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 7 | 7 | 18 | 11 | 6 | 8 | 3 | 18 | 10 | 9 | 10 | 3 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 10 | 15 | 11 | 11
Viscosity | No Sediment or precipitable sludge should be detectable | [8 empty] | Viscosity | 27 CST(Max) | [6 empty] | Viscosity |  |  |  |  | Viscosity | 27 CST(Max) | [18 empty] | Viscosity | 27 CST(Max)
Remarks |  |  | Send sample again after one month for DGA. | [6 empty] | Remarks | [7 empty] | Remarks |  |  | Sampling error suspected.Sample to be sent again for testing. |  | Remarks |  | 2008-05-31: Pls furnish DOC of the transformer.; 2015-08-12: The gases are within limits; 2015-11-02: Gases are within the permissible limits.; 2017-08-05: Send sample again after one month for DGA. | [5 empty] | Remarks | [8 empty] | The gases are within limits | Gases are within the permissible limits. |  | Send sample again after one month for DGA.

## 220KV EDC
Name Of Station : GIS(East Division) |  | Capacity : 150MVA |  |  | Serial Number : 13074-002 | [10 empty] | Name Of Station : GIS(East Division) |  | Capacity : 150MVA |  |  | Serial Number : 13074-001 | [13 empty] | Name Of Station : GIS(East Division) |  | Capacity : 31.5MVA |  |  | Serial Number : 2970 | [10 empty] | Name Of Station : GIS(East Division) |  | Capacity : 31.5MVA |  |  | Serial Number : 2971
SSMD : GIS |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 20-Dec-10 | [10 empty] | SSMD : GIS |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 20-Dec-10 | [13 empty] | SSMD : GIS |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 23-Dec-10 | [10 empty] | SSMD : GIS |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 23-Dec-10
Zone : BANGALORE |  | Make : ABB |  |  | YOM : 2008 | [10 empty] | Zone : BANGALORE |  | Make : ABB |  |  | YOM : 2008 | [13 empty] | Zone : BANGALORE |  | Make : EMCO |  |  | YOM : 2008 | [10 empty] | Zone : BANGALORE |  | Make : EMCO |  |  | YOM : 2008
| Permissible limits as per IS 1866:2000 | [7 empty] | Permissible limits as per 1866-2017 | [7 empty] | Permissible limits as per IS 1866:2000 | [8 empty] | Permissible limits as per 1866-2017 | [9 empty] | Permissible limits as per IS 1866:2000 | [7 empty] | Permissible limits as per 1866-2017 | [7 empty] | Permissible limits as per IS 1866:2000 | [5 empty] | Permissible limits as per 1866-2017
Last Filtn. Date |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | Last Filtn. Date |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | Last Filtn. Date |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | Last Filtn. Date |  | 2010 | 2010 | 2010 | 2010 | 2010 |  | 2010 | 2010 | 2010 | 2010 | 2010
Sampling Date | [15 empty] | Sampling Date | [18 empty] | Sampling Date | [15 empty] | Sampling Date
Date of Test | Permissible limits as per IS 1866:2000 | 2012-05-02 | 2013-04-29 | 2015-07-14 | 2016-06-25 | 2017-05-31 | 2020-07-22 | 2020-12-29 | Vol Class Good Fair Poor | 2021-08-07 | 2022-01-05 | 2022-10-12 | 2023-09-13 | 2024-10-01 | 17/02/2026 | Date of Test | Permissible limits as per IS 1866:2000 | 2012-05-02 | 2013-04-29 | 2015-07-14 | 2016-06-25 | 2016-10-28 | 2017-05-31 | 2018-01-09 | 2020-07-22 | Vol Class Good Fair Poor | 2021-08-07 | 2022-01-05 | 2022-10-12 | 2023-01-23 | 2023-06-13 | 2023-08-23 | 2024-10-01 | 17/02/2026 | Date of Test | Permissible limits as per IS 1866:2000 | 2012-05-04 | 2013-05-17 | 2015-07-14 | 2016-06-25 | 2016-10-28 | 2017-05-31 | 2020-07-22 | Vol Class Good Fair Poor | 2021-08-07 | 2021-12-15 | 2022-11-25 | 2023-06-13 | 2024-10-01 | 2026-02-17 | Date of Test | Permissible limits as per IS 1866:2000 | 2012-05-04 | 2013-05-17 | 2016-06-25 | 2017-06-01 | 2020-07-22 | Vol Class Good Fair Poor | 2021-08-07 | 2022-11-25 | 2024-04-03 | 2024-10-01 | 2026-02-17
Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0029 | 0.01893 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0147 | 0.0081 | 0.0095 | 0.0158 | 0.0138 | 0.00281 | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0068 | 0.0062 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0174 | 0.0411 | 0.0083 |  |  |  | 0.0066 | 0.0089 | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0064 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0251 | 0.0167 | 0.0092 | 0.0081 | 0.015 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.0018 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0132 | 0.008 | 0.0166 | 0.0099 | -
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 90.9 | 122 | 202.7 | 119.5 | 212.1 | 112.08 | 88.65 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 810 | 975 | 1065 | 1300 | 1400 | 1246 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 189 | 122 | 226.4 | 158.9 | 49.63 | 96.04 | 64.83 | 109.6 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 910 | 980 | 720 |  |  |  | 700 | 1100 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 97.3 | 44.9 | 284.2 | 271.4 | 46.46 | 167.7 | 167.42 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1760 | 1630 | 1500 | 500 | 1200 | 950 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 119 | 17.5 | 133.5 | 154.6 | 142.21 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1220 | 1100 | 1092 | 1086 | 950
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0006 | 0.0002 | 0.00086 | 0.00107 | 0.00096 | 0.00177 | 0.00036 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00083 | 0.00035 | 0.0005 | 0.000494 | 0.00065 | 0.00916 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0004 | 0.0002 | 0.00041 | 0.00064 | 0.00022 | 0.00062 | 0.00014 | 0.00559 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.0006 | 0.00029 | 0.0004 |  |  |  | 0.00041 | 0.0094 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0006 | 0.0008 | 0.00038 | 0.00079 | 0.00039 | 0.00027 | 0.00085 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00038 | 0.00083 | 0.000445 | 0.000658 | 0.00058 | 0.00086 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0005 | 0.0018 | 0.00037 | 0.00034 | 0.00111 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00039 | 0.000618 | 0.00059 | 0.00052 | 0.00074
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [7 empty] | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 58 | 86 | 65 | 45 |  | 85 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [8 empty] | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 32 | 64 | 49 | 65 |  |  |  | 82 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [7 empty] | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  |  | 27 | 46 |  |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [5 empty] | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 58 | 42
BDV (B) |  | 55 | 76 | 69 | 30 | 76 | 50 | 57 |  | 40 | 81 | 61 | 44 | 97 | 89 | BDV (B) |  | 82 | 76 | 50 | 31 | 28 | 56 | 74 | 52 |  | 19 | 62 | 42 | 36 | 38 | 64 | 77 | 73 | BDV (B) |  | 54 | 65 | 20 | 15 | 36 | 39 | 38 |  | 33 | 30 | 25 | 43 | 73 | 70 | BDV (B) |  | 57 | 72 | 31 | 57 | 53 |  | 52 | 37 | 69 | 85 | 76
IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35.18 | 38.63 | 32.92 | >25 20-25 <20 (for all voltage class) | 35.72 | 36.59 | 37.85 | 37.89 | 32.5 | 37.62 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35.21 | 28.37 | 39.73 | >25 20-25 <20 (for all voltage class) | 34.3 | 28.84 | 40.02 |  |  |  | 33.68 | 36.81 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 41.08 | 40.39 | >25 20-25 <20 (for all voltage class) | 36.78 | 35.82 | 38.7 | 38 | 31.82 | 31.51 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 44 | 41.67 | >25 20-25 <20 (for all voltage class) | 39.1 | 36.1 | 35.62 | 32.19 | 38.09
F P | 125° C (Min) | 161 | 149 | 149 | 151 | 168 | 156 | 155 | Max decrease 10% (for all class of Voltage) | 164 | 166 | 160 | 172 | 161 | 151 | F P | 125° C (Min) | 161 |  | 160 | 149 | 156 | 170 | 152 | 155 | Max decrease 10% (for all class of Voltage) | 169 | 166 | 171 |  |  |  | 157 | 157 | F P | 125° C (Min) | 159 | 151 | 150 | 170 | 152 | 176 | 158 | Max decrease 10% (for all class of Voltage) | 160 | 161 | 164 | 160 | 160 | 170 | F P | 125° C (Min) | 161 | 153 | 151 | 169 | 165 | Max decrease 10% (for all class of Voltage) | 162 | 159 | 159 | 160 | 152
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 3 | 11 | 8 | 13 | 7 | 12 | 8 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 5 | 11 | 19 | 11 | 6 | 8 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 5 | 11 | 11 | 9 | 5 | 5 | 1 | 8 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 20 | 15 | 23 | 7 | 20 | 11 | 12 | 6 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 12 | 12 | 21 | 53 | 14 | 28 | 25 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 25 | 35 | 36 | 26 | 15 | 17 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 11 | 10 | 19 | 13 | 14 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 11 | 23 | 14 | 10 | 11
Remarks |  |  |  | Gases are within the permissible limits. When compared to previous test results there is variation in respect of resistivity & tan delta values.Clarify whether oil has been topped up? | Sed oil sample again within a month. | [10 empty] | Remarks |  | 2015-07-14: Gases are within the permissible limits.When compared to previous test results there is variation in respect of resistivity & tan delta values.Clarify whether oil has been topped up?; 2016-06-25: Send oil sample again within a month.; 2016-10-28: Send oil sample again within a month. |  | Send sample again after 2 month. | [7 empty] | Remarks |  |  |  | Gases are within the permissible limits.When compared to previous test results there is variation in respect of resistivity & tan delta values.Clarify whether oil has been topped up? | Send oil sample again within a month. | Variation in respect of resistivity and tan-delta values is observed clarify. |  |  |  | Send sample again after 2 month. | DGA test not carried out due to equipment under repair. |  |  |  |  | Remarks

## 220 KV Jigani
Name Of Station : Jigani |  | Capacity : 150MVA |  |  | Serial Number : 13068-006 | [7 empty] | Name Of Station : Jigani |  | Capacity : 150MVA |  | Serial Number : 13068-005 | [5 empty] | Name Of Station : Jigani |  | Capacity : 31.5MVA |  |  | Serial Number : 4-0012/6 | [11 empty] | Name Of Station : Jigani |  | Capacity : 31.5MVA |  |  | Serial Number : 4934/17
SSMD : Yerandanahalli |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 15-Nov-19 | [7 empty] | SSMD : Yerandanahalli |  | Voltage Class : 220/66 KV |  | Date Of Commission : 04-Mar-18 | [5 empty] | SSMD : Yerandanahalli |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 30-Sep-11 | [11 empty] | SSMD : Yerandanahalli |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 03-Nov-22
Zone : BANGALORE |  | Make : ABB |  |  | YOM : 2008 | [7 empty] | Zone : BANGALORE |  | Make : ABB |  | YOM : 2008 | [5 empty] | Zone : BANGALORE |  | Make : VICTORY |  |  | YOM : 2009 | [11 empty] | Zone : BANGALORE |  | Make : BBL/KK RAO |  |  | YOM : 2006/2022
| Permissible limits as per IS 1866:2000 | [12 empty] | Permissible limits as per IS 1866:2000 | [9 empty] | Permissible limits as per IS 1866:2000 | [16 empty] | Permissible limits as per IS 1866:2000
Last Filtn. Date |  | 2019 | 2019 | Permissible limits as per 1866-2017 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | 2019 | Last Filtn. Date |  | 2018 | Permissible limits as per 1866-2017 |  | 2018 | 2018 | 2018 | 2018 | 2018 | Last Filtn. Date |  | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | Permissible limits as per 1866-2017 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | Last Filtn. Date |  | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | Permissible limits as per 1866-2017 | 2006 | 2022 | 2022 | 2022
Sampling Date | [12 empty] | Sampling Date | [9 empty] | Sampling Date | [16 empty] | Sampling Date
Date of Test | Permissible limits as per IS 1866:2000 | 2020-08-07 | 2020-12-15 | Vol Class Good Fair Poor | 2021-08-06 | 2022-08-17 | 2022-09-08 | 2022-09-14 | 2022-09-19 | 2023-09-14 | 2024-11-16 | 2026-04-17 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-08-07 | Vol Class Good Fair Poor |  | 2021-08-06 | 2022-08-17 | 2023-09-14 | 2024-11-16 | 2026-04-17 | Date of Test | Permissible limits as per IS 1866:2000 | 2012-01-02 | 2013-12-07 | 2015-02-18 | 2015-08-18 | 2016-07-14 | 2017-07-12 | 2020-08-07 | Vol Class Good Fair Poor | 2021-08-07 | 2022-08-17 | 2022-09-14 | 2022-12-08 | 2023-09-14 | 2024-11-16 | 2026-04-17 | Date of Test | Permissible limits as per IS 1866:2000 | 2007-08-31 | 2008-08-25 | 2008-08-26 | 2008-12-03 | 2010-02-06 | 2011-05-27 | 2012-06-12 | 2013-07-09 | 2014-05-13 | 2015-07-31 | 2016-06-16 | 2017-06-06 | Vol Class Good Fair Poor | 2021-08-03 | 2023-09-14 | 2024-11-16 | 2026-04-17
Aci dity | 0.3 mg KOH / gm(Max) | 0.0054 | 0.0081 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0041 | 0.017 | 0.0051 | 0.0093 | 0.0065 | 0.009 | 0.0087 | 0.006 | Aci dity | 0.3 mg KOH / gm(Max) | 0.0104 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 |  | 0.0025 | 0.0122 | 0.0076 | 0.0104 | 0.0072 | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0326 | 0.0089 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0251 | 0.109 | 0.0114 | 0.0096 | 0.0099 | 0.0118 | 0.0068 | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0036 | 0.0063 | 0.0098 | 0.0098
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 78.31 | 100.7 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1400 | 1660 | 1770 | 1900 | 450 | 1400 | 1600 | 1660 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 82.92 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 |  | 1440 | 1459 | 1300 | 1450 | 1450 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 189 | 154 | 153 | 109.6 | 156.5 | 135.7 | 173.4 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1560 | 1850 | 820 | 1456 | 1260 | 1300 | 1300 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 1.39 | 28.1 | 29.1 | 81 | 77.8 | 69.3 | 90.6 | 85 | 84.8 | 84 | 163.3 | 148.2 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1400 | 1360 | 1240 | 916.1
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00191 | 0.00096 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.000418 | 0.00043 | 0.000665 | 0.000527 | 0.001378 | 0.000878 | 0.00068 | 0.000571 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0006 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  | 0.000293 | 0.0059 | 0.00051 | 0.00068 | 0.00428 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.05 | 0.0007 | 0.0007 | 0.00128 | 0.00047 | 0.00088 | 0.00072 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.000494 | 0.00066 | 0.000487 | 0.00087 | 0.0006 | 0.00076 | 0.000857 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0042 | 0.003 | 0.0028 | 0.0017 | 0.0015 | 0.0009 | 0.0006 | 0.0006 | 0.0012 | 0.0013 | 0.00045 | 0.0002 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00648 | 0.00041 | 0.00041 | 0.000926
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  |  |  | 62 |  | 50 | 47 | 70 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  |  |  | 52 | 57 | 70 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 63 | [6 empty] | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  |  | 46 |  | 47 | 47 | 30 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 2008-08-26: 74 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 55 | 41 | 31
BDV (B) |  | 52 | 51 |  | 45 | 17 | 38 | 54 | 52 | 48 | 48 | 80 | BDV (B) |  | 51 |  |  | 58 | 79 | 50 | 51 | 82 | BDV (B) |  | 54 | 74 | 65 | 34 | 42 | 33 | 32 |  | 35 | 33 | 28 | 44 | 43 | 28 | 58 | BDV (B) |  | 61 | 10 | 66 | 45 | 66 | 57 | 69 | 48 | 75 | 63 | 36 | 30 |  | 37 | 53 | 37 | 70
IFT | 15 Dynes / cm (Min) | 42.73 | 37.08 | >25 20-25 <20 (for all voltage class) | 36.1 | 36.13 | 36.02 | 34.76 | 36.89 | 33.52 | 36.19 | 36.11 | IFT | 15 Dynes / cm (Min) | 38.5 | >25 20-25 <20 (for all voltage class) |  | 35.7 | 35.85 | 36.2 | 34.64 | 34 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 39.41 | 40 | >25 20-25 <20 (for all voltage class) | 34.86 | 34.76 | 33.17 | 31.52 | 35.11 | 32.62 | 33.1 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40.15 | >25 20-25 <20 (for all voltage class) | 34.26 | 34.29 | 37.62 | 38.14
F P | 125° C (Min) | 172 | 155 | Max decrease 10% (for all class of Voltage) | 161 | 158 | 162 | 158 | 162 | 166 | 159 | 165 | F P | 125° C (Min) | 176 | Max decrease 10% (for all class of Voltage) |  | 35.7 | 162 | 151 | 159 | 170 | F P | 125° C (Min) | 159 | 157 | 156 | 156 | 160 | 175 | 166 | Max decrease 10% (for all class of Voltage) | 164 | 165 | 160 | 164 | 162 | 165 | 152 | F P | 125° C (Min) | 169 |  |  |  | 147 | 147 | 167 | 159 | 157 | 156 | 148 | 176 | Max decrease 10% (for all class of Voltage) | 160 | 171 | 168 | 149
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 10 | 11 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 16 | 9 | 19 | 15 | 15 | 14 | 15 | 8 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 12 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 |  | 8 | 7 | 17 | 19 | 9 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 11 | 9 | 7 | 31 | 19 | 35 | 24 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 14 | 17 | 27 | 24 | 21 | 25 | 25 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 15 | 17 | 7 | 12 | 10 | 14 | 27 | 4 | 10 | 21 | 18 | 19 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 21 | 19 | 24 | 22
Remarks | [12 empty] | Remarks | [9 empty] | Remarks |  |  |  |  | The gases are within limits | [11 empty] | Remarks |  | 2008-08-25: Sampling error is suspected. Send oil sample again as per the sampling guidelines.; 2008-12-03: Flash Point test is nto carried out due to Equipment fault. When compared to previous test results there is variation in respect of Resistivity & Tan-Delta.; 2012-06-12: Compared to previous test result there is variation in respect of tan delta & resistivity values.Please verify/analyze.; 2015-07-31: The gases evolved are within limits.; 2017-06-06: Furnish the last date of filtration.

## 220KV KANAKAPURA
Name Of Station : Kanakapura 220kV |  | Capacity : 100MVA |  |  | Serial Number : 13044-002 | [12 empty] | Name Of Station : Kanakapura 220kV |  | Capacity : 100MVA |  |  | Serial Number : 2141612
SSMD : Somanahalli |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 31-Dec-07 | [12 empty] | SSMD : Kanakapura |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 22-11-2016
Zone : BANGALORE |  | Make : ABB |  |  | YOM : 2007 | [12 empty] | Zone : BANGALORE |  | Make : BHEL |  |  | YOM : 2015
| Permissible limits as per IS 1866:2000 | [12 empty] | Permissible limits as per 1866-2017 |  |  |  |  | Permissible limits as per IS 1866:2000 | [5 empty] | Permissible limits as per 1866-2017
Last Filtn. Date |  | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 |  | 2007 | 2007 | 2007 | 2007 | 2007 | Last Filtn. Date |  | 2016 | 2016 | 2016 |  | 2016 | 2016 | 2016 | 2016 | 2016
Sampling Date | [17 empty] | Sampling Date
Date of Test | Permissible limits as per IS 1866:2000 | 2009-06-25 | 2009-12-18 | 2011-09-29 | 2013-09-16 | 2014-06-16 | 2015-08-11 | 2016-08-29 | 2017-09-06 | 2020-07-16 | 2020-10-15 | Vol Class Good Fair Poor | 2021-07-27 | 2022-10-13 | 2023-11-23 | 2025-01-20 | 2026-04-23 | Date of Test | Permissible limits as per IS 1866:2000 | 2017-09-06 | 2020-07-16 | 2020-10-15 | Vol Class Good Fair Poor | 2021-07-27 | 2022-10-13 | 2023-11-23 | 2025-01-20 | 2026-04-23
Aci dity | 0.3 mg KOH / gm(Max) | 0.006 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0128 | 0.0281 | 0.0053 |  | 0.0213 | 0.0089 | 0.0102 | 0.0142 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.0128 | 0.0083 | 0.0071 |  | 0.0087 | 0.0076 | 0.0092 | 0.0171 | -
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 24.8 | 26.1 | 87.8 | 217.3 | 212.4 | 182.7 | 45.4 | 130.1 | 187.5 | 132.1 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 92.06 | 1400 | 1490 | 1200 | 966.1 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 130.1 | 148 | 104.6 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 90 | 1500 | 1123 | 730 | 896.6
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0023 | 0.0019 | 0.0008 | 0.0001 | 0.0005 | 0.00077 | 0.00106 | 0.00025 | 0.00179 | 0.0016 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.00051 | 0.0041 | 0.00104 | 0.000692 | 0.0021 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00025 | 0.00059 | 0.00048 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.000716 | 0.0005 | 0.00075 | 0.00916 | 0.00261
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 2009-06-25: 24; 2009-12-18: 60; 2013-09-16: 73; 2020-07-16: 43; 2020-10-15: 31 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 52 | 52 | 66 | 62 | 88 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  | 39 | 36 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 64 | 64 | 26 | 20 | 53
BDV (B) |  | 23 | 52 | 65 | 60 | 53 | 58 | 21 | 63 | 35 | 25 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 43 | 46 | 63 | 22 | 65 | BDV (B) |  | 63 | 24 | 30 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 63 | 58 | 23 | 40 | 44
IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 33.97 | 36.28 | 35.1 | >25 20-25 <20 (for all voltage class) | 34.68 | 33.12 | 32.28 | 35.11 | 35.6 | IFT | 15 Dynes / cm (Min) | 38.97 | 37.1 | 36.85 | >25 20-25 <20 (for all voltage class) | 37.08 | 34.4 | 37.59 | 34.73 | 35.6
F P | 125° C (Min) | 157 | 163 | 158 | 160 | 159 | 157 | 158 | 152 | 157 | 166 | Max decrease 10% (for all class of Voltage) | 170 | 160 | 169 | 163 | 172 | F P | 125° C (Min) | 152 | 175 | 168 | Max decrease 10% (for all class of Voltage) | 175 | 169 | 172 | 149 | 169
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 19 | 4 | 5 | 4 | 5 | 20 | 23 | 11 | 24 | 16 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 12 | 21 | 22 | 55 | 9 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 11 | 30 | 15 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 12 | 18 | 39 | 20 | 26
Remarks |  | Send oil sample again as per the sampling guidelines. |  | When compared to previous test results there is variation in respect of tan-delta & resistivity values. | When compared with previous test results, tere is variation in respect of Resistivity & Tan-Delta. |  | The gases are within limits | Send oil sample again within a month. | Send oil sample again within a month for DGA. | Sampling error suspected. | Sampling error suspected. | [6 empty] | Remarks |  | Send oil sample again within a month for DGA. | Sampling error suspected. | Sampling error suspected.

## 220 KV MANYATHA
Name Of Station : GIS Manyatha Tech Park |  | Capacity : 31.5MVA |  | Serial Number : ITK/53555 |  |  |  | Name Of Station : GIS Manyatha Tech Park |  | Capacity : 31.5MVA |  | Serial Number : ITK53553 |  |  |  | Name Of Station : GIS Manyatha Tech Park |  | Capacity : 31.5MVA |  | Serial Number : ITK-53554 |  |  |  |  | Name Of Station : GIS Manyatha Tech Park |  | Capacity : 31.5MVA |  | Serial Number : ITK-53552
SSMD : Bangalore |  | Voltage Class : 66/11 KV |  | Date Of Commission : 20-May-19 |  |  |  | SSMD : Bangalore |  | Voltage Class : 66/11 KV |  | Date Of Commission : 20-May-19 |  |  |  | SSMD : Bangalore |  | Voltage Class : 66/11 KV |  | Date Of Commission : 20-May-19 |  |  |  |  | SSMD : Bangalore |  | Voltage Class : 66/11 KV |  | Date Of Commission : 20-May-19
Zone : BANGALORE |  | Make : INDO TECH |  | YOM : 2017 |  |  |  | Zone : BANGALORE |  | Make : INDO TECH |  | YOM : 2017 |  |  |  | Zone : BANGALORE |  | Make : INDO TECH |  | YOM : 2017 |  |  |  |  | Zone : BANGALORE |  | Make : INDO TECH |  | YOM : 2017
| Permissible limits as per IS 1866:2000 |  | Permissible limits as per 1866-2017 | [5 empty] | Permissible limits as per IS 1866:2000 |  | Permissible limits as per 1866-2017 | [5 empty] | Permissible limits as per IS 1866:2000 |  | Permissible limits as per 1866-2017 | [6 empty] | Permissible limits as per IS 1866:2000 |  | Permissible limits as per 1866-2017
Last Filtn. Date |  | 2019 |  | 2019 | 2019 | 2019 | 2019 | Last Filtn. Date |  | 2019 |  | 2019 | 2019 | 2019 | 2019 | Last Filtn. Date |  | 2019 |  | 2019 | 2019 | 2019 | 2019 | 2019 | Last Filtn. Date |  | 2019 |  | 2019 | 2019 | 2019 | 2019 | 2019
Sampling Date | [7 empty] | Sampling Date | [7 empty] | Sampling Date | [8 empty] | Sampling Date
Date of Test | Permissible limits as per IS 1866:2000 | 2020-09-08 | Vol Class Good Fair Poor | 2021-12-13 | 2022-12-05 | 2024-03-28 | 2025-03-20 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-09-08 | Vol Class Good Fair Poor | 2021-12-13 | 2022-12-03 | 2024-03-28 | 2025-03-20 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-09-08 | Vol Class Good Fair Poor | 2021-12-13 | 2022-12-03 | 2023-01-04 | 2024-03-28 | 20/03/2025 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-09-08 | Vol Class Good Fair Poor | 2021-12-13 | 2022-12-01 | 2022-12-03 | 2024-03-28 | 2025-03-20
Aci dity | 0.3 mg KOH / gm(Max) | 0.0059 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.00062 | 0.016 | 0.0092 | 0.0048 | Aci dity | 0.3 mg KOH / gm(Max) | 0.0057 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0064 | 0.0083 | 0.0079 | 0.0061 | Aci dity | 0.3 mg KOH / gm(Max) | 0.0084 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0089 | 0.0092 |  | 0.0102 | 0.0069 | Aci dity | 0.3 mg KOH / gm(Max) | 0.0064 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0069 | 0.0086 | 0.0086 | 0.0091 | 0.0052
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 293.4 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 3100 | 1800 | 1650 | 1460 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 192.3 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 2160 | 1400 | 1529 | 1380 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 142.2 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1700 | 1480 |  | 1280 | 1366 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 192.3 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 2000 | 1640 | 1640 | 1300 | 1432
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00045 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.000383 | 0.000469 | 0.000568 | 0.00081 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00078 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.000322 | 0.000467 | 0.00098 | 0.00081 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00065 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.000524 | 0.000524 |  | 0.000891 | 0.0091 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00088 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.000462 | 0.000975 | 0.000975 | 0.000587 | 0.0092
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  |  |  |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 38 |  |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 31 | 76 |  |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 38 | 38
BDV (B) |  | 40 |  | 33 | 39 | 70 | 91 | BDV (B) |  | 41 |  | 65 | 27 | 65 | 56 | BDV (B) |  | 60 |  | 28 | 25 | 69 | 92 | 64 | BDV (B) |  | 40 |  | 26 | 36 | 36 | 54 | 40
IFT | 15 Dynes / cm (Min) | 41.26 | >25 20-25 <20 (for all voltage class) | 38.25 | 32.16 | 35.41 | 36.25 | IFT | 15 Dynes / cm (Min) | 35.4 | >25 20-25 <20 (for all voltage class) | 39.26 | 38.56 | 37.17 | 34.14 | IFT | 15 Dynes / cm (Min) | 36.71 | >25 20-25 <20 (for all voltage class) | 37.43 | 39.11 |  | 33.13 | 37.94 | IFT | 15 Dynes / cm (Min) | 34.68 | >25 20-25 <20 (for all voltage class) | 38.8 | 36.79 | 36.79 | 35.6 | 36.1
F P | 125° C (Min) | 171 | Max decrease 10% (for all class of Voltage) | 173 | 160 | 164 | 163 | F P | 125° C (Min) | 168 | Max decrease 10% (for all class of Voltage) | 170 | 168 | 172 | 165 | F P | 125° C (Min) | 159 | Max decrease 10% (for all class of Voltage) | 165 | 162 |  | 167 | 162 | F P | 125° C (Min) | 171 | Max decrease 10% (for all class of Voltage) | 168 | 170 | 170 | 168 | 168
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 8 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 25 | 21 | 10 | 5 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 18 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 8 | 31 | 9 | 7 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 11 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 28 | 30 | 11 | 12 | 18 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 19 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 28 | 33 | 33 | 24 | 7
Remarks | [7 empty] | Remarks | [7 empty] | Remarks | [8 empty] | Remarks

## 220KV KOLAR
Name Of Station : Kolar 220kV |  | Capacity : 100MVA |  |  | Serial Number : 6800000136
SSMD : Kolar |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 07-Sep-21 | [36 empty] | Name Of Station : Kolar |  | Capacity : 20MVA |  |  | Serial Number : 13185 | [22 empty] | Name Of Station : Kolar 220kV |  | Capacity : 20MVA |  | Serial Number : PT-7761 |  |  |  |  | Name Of Station : Kolar 220kV |  | Capacity : 100MVA |  |  | Serial Number : T-8561/1 | [14 empty] | Name Of Station : Kolar 220kV |  | Capacity : 100MVA |  |  | Serial Number : 6800000059
Zone : BANGALORE |  | Make : NGEF |  |  | YOM : 1995 | [36 empty] | SSMD : Kolar |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 26-Mar-04 | [22 empty] | SSMD : Kolar |  | Voltage Class : 66/11 KV |  | Date Of Commission : 22-Aug-17 |  |  |  |  | SSMD : Kolar |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 08-Dec-16 | [14 empty] | SSMD : Kolar |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 21-Aug-89
| Permissible limits as per IS 1866:2000 | [33 empty] | Permissible limits as per 1866-2017 | [6 empty] | Zone : BANGALORE |  | Make : ANDREW YULE |  |  | YOM : 2004 | [22 empty] | Zone : BANGALORE |  | Make : IMP |  | YOM : 2017 |  |  |  |  | Zone : BANGALORE |  | Make : CGL |  |  | YOM : 1997 | [14 empty] | Zone : BANGALORE |  | Make : NGEF |  |  | YOM : 1989
Last Filtn. Date |  | 1996 | 1996 | 1996 | 1996 | 1996 | 1996 | 1996 | 1996 | 1996 | 1996 | 1996 | 1996 | 1996 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 |  | 2021 | 2021 | 2021 | 2021 | 2021 | 2021 | 2023 |  | Permissible limits as per IS 1866:2000 | [22 empty] | Permissible limits as per 1866-2017 |  |  |  |  | Permissible limits as per IS 1866:2000 |  |  |  | Permissible limits as per 1866-2017 |  |  |  |  | Permissible limits as per IS 1866:2000 | [12 empty] | Permissible limits as per 1866-2017 | [6 empty] | Permissible limits as per IS 1866:2000 | [33 empty] | Permissible limits as per 1866-2017
Sampling Date | [41 empty] | Last Filtn. Date |  | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2014 | 2014 | 2014 | 2014 | 2014 | 2014 |  | 2014 | 2014 | 2014 | 2014 | Last Filtn. Date |  | 2017 |  |  | 2017 | 2017 | 2017 | 2017 | Last Filtn. Date | [8 empty] | 2016 | 2016 | 2016 | 2016 |  | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | Last Filtn. Date |  | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 |  | 2017 | 2022 | 2022 | 2022 | 2022 | 2022 | 2022
Date of Test | Permissible limits as per IS 1866:2000 | 2001-03-27 | 2002-02-13 | 2002-07-11 | 2002-09-18 | 2002-10-28 | 2003-01-16 | 2003-06-10 | 2003-07-29 | 2003-08-26 | 2004-03-17 | 2004-11-05 | 2005-03-21 | 2005-12-26 | 2006-03-13 | 2008-02-25 | 2009-05-16 | 2009-12-07 | 2010-03-02 | 2010-11-22 | 2011-05-27 | 2012-04-28 | 2013-08-16 | 2013-12-04 | 2014-05-19 | 2015-06-04 | 2016-07-28 | 2016-08-01 | 2017-05-23 | 2017-07-22 | 2017-12-06 | 2020-07-10 | 2021-02-03 | Vol Class Good Fair Poor | 2021-09-07 | 2023-01-21 | 2023-06-12 | 2023-08-16 | 2023-08-28 | 2024-02-08 | 2025-01-22 | Sampling Date | [27 empty] | Sampling Date | [8 empty] | Sampling Date | [19 empty] | Sampling Date
Aci dity | 0.3 mg KOH / gm(Max) | 0.1 | 0.05 | 0.1 | 0.123 | 0.11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.145 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3 | 0.0472 | 0.1038 | 0.0265 | 0.01435 |  | 0.0438 | 0.0546 | 0.031 | 0.0159 | 0.0109 | 0.0197 | 0.0134 | Date of Test | Permissible limits as per IS 1866:2000 | 2004-11-18 | 2005-01-31 | 2005-07-07 | 2006-06-17 | 2006-07-07 | 2006-08-11 | 2006-10-09 | 2007-09-19 | 2007-11-22 | 2009-02-02 | 2009-04-24 | 2010-05-26 | 2010-06-18 | 2011-01-28 | 2013-08-04 | 2014-05-26 | 2014-06-11 | 2015-06-30 | 2016-06-10 | 2017-12-28 | 2020-08-27 | Vol Class Good Fair Poor | 2021-09-30 | 2023-01-24 | 2024-02-09 | 2025-01-21 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-08-27 | Vol Class Good Fair Poor |  | 2021-09-30 | 2023-01-24 | 2024-02-09 | 2025-01-21 | Date of Test | Permissible limits as per IS 1866:2000 | 2001-01-04 | 2002-01-30 | 2002-05-10 | 2004-06-08 | 2004-06-24 | 2010-05-18 | 2010-06-11 | 2016-10-27 | 2017-12-28 | 2020-08-27 | 2021-03-23 | Vol Class Good Fair Poor | 2021-09-30 | 2022-04-29 | 2022-06-18 | 2023-01-21 | 2024-02-09 | 2025-01-27 | Date of Test | Permissible limits as per IS 1866:2000 | 1998-06-22 | 1999-01-25 | 1999-02-15 | 2000-04-22 | 2000-05-26 | 2001-12-20 | 2002-09-17 | 2004-11-18 | 2005-01-29 | 2005-07-14 | 2006-01-06 | 2006-08-24 | 2006-10-31 | 2007-05-19 | 2007-11-14 | 2009-02-13 | 2010-05-31 | 2011-07-27 | 2012-06-23 | 2013-05-24 | 2014-05-26 | 2014-08-11 | 2015-08-11 | 2016-06-09 | 2016-09-20 | 2017-01-24 | 2017-01-25 | 2017-04-24 | 2017-12-28 | 2019-10-14 | 2020-04-28 | 2020-08-27 | Vol Class Good Fair Poor | 2021-09-30 | 2022-02-18 | 2022-06-20 | 2023-01-20 | 2023-06-12 | 2024-02-08 | 2025-01-22
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 2.97 | 1.5 | 0.299 | 1.12 | 0.449 | 1.46 | 1.12 | 1.25 | 1.29 | 1.25 | 1.41 | 1.38 | 1.24 | 0.921 | 0.719 | 0.709 | 0.694 | 0.693 | 0.711 | 0.704 | 0.691 | 0.652 | 0.651 | 0.632 | 0.621 | 0.4785 | 0.5521 | 0.4224 | 0.3852 | 0.3586 | 0.4952 | 0.379 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 38 | 1200 | 8.5 | 2400 | 460 | 240 | 340 | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.006 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0315 | 0.0148 |  | 0.0151 | 0.0281 | 0.0109 | 0.017 | Aci dity | 0.3 mg KOH / gm(Max) | 0.0067 |  |  | 0.0082 | 0.0166 | 0.0085 | 0.0255 | Aci dity | 0.3 mg KOH / gm(Max) | 0.2 | 0.1 | 0.05 | 0.1 | 0.1 | 0.01 | 0.05 | 0.02 | 0.022 | 0.0115 | 0.0082 |  | 0.0091 | 0.0107 | 0.0076 | 0.0177 | 0.0069 | 0.0181 | Aci dity | 0.3 mg KOH / gm(Max) | 0.1 | 0.2 | 0.2 | 0.05 | 0.1 | 0.1 | 0.28 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.05 | 0.3 | 0.3 | 0.0335 | 0.0116 | 0.0368 | 0.0978 |  | 0.0989 | 0.0042 | 0.0468 | 0.0651 | 0.0298 | 0.0279 | 0.0295
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0086 | 0.019 | 0.081 | 0.025 | 0.051 | 0.017 | 0.021 | 0.024 | 0.0249 | 0.02 | 0.0164 | 0.0201 | 0.0258 | 0.033 | 0.04 | 0.043 | 0.051 | 0.053 | 0.044 | 0.048 | 0.051 | 0.034 | 0.035 | 0.04 | 0.04 | 0.07 | 0.0602 | 0.0419 | 0.0427 | 0.064 | 0.6842 | 0.0461 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.0024 | 0.00041 | 0.0298 | 0.000584 | 0.0017 | 0.00351 | 0.00264 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 49.1 | 34.1 | 32.9 | 34.9 | 57.1 | 56.8 | 52.8 | 48.6 | 47.1 | 46.8 | 46.9 | 47.3 | 48.4 | 68.1 | 98.2 | 95.1 | 64.53 | 64 | 59.7 | 65.13 | 138.4 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 679.1 | 390 | 830 | 710 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 145.83 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 |  | 1337 | 1350 | 1500 | 1200 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 6.54 | 4.13 | 46.3 | 1.84 | 17.4 | 70.9 | 47.3 | 58.85 | 55.87 |  | 100.4 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 900 | 780 | 1700 | 1200 | 1600 | 1461 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 0.256 | 0.138 | 0.396 | 0.0932 | 0.0985 | 1.63 | 1.43 | 1.19 | 0.741 | 1.06 | 1.12 | 1.1 | 1.24 | 1.31 | 0.801 | 0.803 | 0.797 | 0.763 | 0.743 | 0.538 | 0.529 | 0.525 | 0.391 | 0.403 | 0.2426 | 0.2297 | 0.2094 | 0.1991 | 0.1944 | 0.1911 | 0.375 | 0.1693 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 1.9 | 2.401 | 9 | 9.5 | 14 | 7.5 | 9
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 2006-03-13: 89; 2009-12-07: 62; 2010-03-02: 50; 2010-11-22: 31; 2012-04-28: 54; 2013-08-16: 51; 2016-08-01: 88; 2020-07-10: 66; 2021-02-03: 41 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 78 | 56 | 36 |  | 63 | 30 | 39 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0021 | 0.003 | 0.0032 | 0.0005 | 0.0001 | 0.0004 | 0.0006 | 0.0009 | 0.0009 | 0.0009 | 0.0009 | 0.0009 | 0.0008 | 0.0006 | 0.0005 | 0.001 | 0.003 | 0.0034 | 0.00099 | 0.00019 | 0.00043 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.00132 | 0.00176 | 0.000841 | 0.0057 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00107 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 |  | 0.0004 | 0.00179 | 0.000473 | 0.00054 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0079 | 0.013 | 0.001 | 0.018 | 0.0021 | 0.0009 | 0.0015 | 0.0006 | 0.00082 |  | 0.0004 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.00081 | 0.0001 | 0.000293 | 0.00041 | 0.000411 | 0.00413 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.092 | 0.134 | 0.0055 | 0.21 | 0.207 | 0.016 | 0.017 | 0.0248 | 0.034 | 0.019 | 0.022 | 0.027 | 0.0261 | 0.026 | 0.031 | 0.032 | 0.035 | 0.039 | 0.041 | 0.039 | 0.048 | 0.051 | 0.0738 | 0.089 | 0.0628 | 0.0684 | 0.0697 | 0.1058 | 0.1087 | 0.0982 | 0.012 | 0.0961 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.0843 | 0.1503 | 0.02698 | 0.0258 | 0.02267 | 0.03506 | 0.04301
BDV (B) |  | 86 | 40 | 65 | 66 | 57 | 69 | 43 | 42 | 64 | 81 | 56 | 47 | 11 | 63 | 68 | 64 | 33 | 44 | 25 | 50 | 50 | 29 | 52 | 50 | 50 | 50 | 65 | 38 | 60 | 17 | 62 | 39 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 71 | 52 | 35 | 25 | 61 | 27 | 37 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  | 73 | 65 | [11 empty] | 60 |  |  |  | 58 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  |  |  |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 58 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | [5 empty] | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 37 |  |  | 54 | 69 | 68 |  | 80 |  | 58 | 65 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 60 | 29 | 54 | 29 | 57 | 54 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 60 |  |  | 15 |  |  |  |  | 71 | [10 empty] | 65 | 36 | [6 empty] | 67 |  |  | 55 | 45 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 68 | 44 | 73 | 51 | 44 | 42 | 42
IFT | 15 Dynes / cm (Min) | 30 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 15 | 15 | 19.09 | 18.8 | 16.85 | 19.28 | >25 20-25 <20 (for all voltage class) | 16.49 | 16.49 | 18.82 | 27.4 | 33.42 | 24.39 | 32.83 | BDV (B) |  | 25 | 37 | 37 | 55 | 53 | 55 | 35 | 47 | 30 | 52 | 43 | 39 | 30 | 44 | 24 | 52 | 59 | 31 | 33 | 54 | 56 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 52 | 38 | 39 | 30 | BDV (B) |  | 56 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 53 | 49 | 39 | 58 | BDV (B) |  | 22 | 17 | 86 | 54 | 59 | 64 | 63 | 76 | 55 | 56 | 51 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 58 | 37 | 46 | 24 | 54 | 37 | BDV (B) |  | 39 | 39 | 60 | 15 | 24 | 66 | 52 | 29 | 43 | 42 | 52 | 59 | 61 | 56 | 84 | 38 | 53 | 69 | 50 | 59 | 32 | 29 | 45 | 66 | 20 | 56 | 74 | 42 | 68 | 38 | 49 | 37 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 66 | 39 | 64 | 50 | 39 | 40 | 29
F P | 125° C (Min) |  | 161 | 146 | 160 | 146 | 146 | 162 | 176 |  | 161 | 158 |  |  |  |  | 167 | 175 | 167 | 175 | 167 | 165 | 163 | 163 | 161 | 159 | 166 | 161 | 173 | 170 | 170 | 156 | 163 | Max decrease 10% (for all class of Voltage) | 163 | 164 | 168 | 166 | 167 | 171 | 158 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 39.13 | 36.28 | >25 20-25 <20 (for all voltage class) | 30.92 | 32.95 | 35.88 | 38.71 | IFT | 15 Dynes / cm (Min) | 36.28 | >25 20-25 <20 (for all voltage class) |  | 32.16 | 35.42 | 35.38 | 33.42 | IFT | 15 Dynes / cm (Min) | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 33.96 | 36.28 | 38.88 | >25 20-25 <20 (for all voltage class) | 37.25 | 38.98 | 36.15 | 36.42 | 37.99 | 38.82 | IFT | 15 Dynes / cm (Min) | 20 |  | 20 |  |  | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 20 | 20 | 15 | 15 | 35 | 15 | 19.1 | 19.21 | 18.9 | 18.08 | 16.91 | >25 20-25 <20 (for all voltage class) | 15.68 | 24 | 21.15 | 19.42 | 20.22 | 16.49 | 15.68
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) |  |  |  |  | 22 | 9 | 31 | 31 | 20 | 18 | 31 | 26 | 69 | 13 | 16 | 24 | 28 | 18 | 16 | 20 | 20 | 18 | 18 | 20 | 20 | 37 | 19 | 23 | 18 | 39 | 36 | 36 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 10 | 45 | 39 | 28 | 9 | 29 | 50 | F P | 125° C (Min) | 158 | 158 | [5 empty] | 151 | 149 |  |  | 157 | 157 | 137 | 144 | 149 | 145 | 146 | 153 | 170 | 166 | Max decrease 10% (for all class of Voltage) | 158 | 160 | 159 | 154 | F P | 125° C (Min) | 166 | Max decrease 10% (for all class of Voltage) |  | 161 | 167 | 159 | 162 | F P | 125° C (Min) |  | 145 | 147 |  |  | 169 | 167 | 170 | 176 | 166 | 165 | Max decrease 10% (for all class of Voltage) | 162 | 166 | 176 | 172 | 164 | 160 | F P | 125° C (Min) | [6 empty] | 171 | 174 | 174 |  |  |  |  | 169 | 169 |  | 167 | 167 | 167 | 165 | 165 | 161 | 159 | 167 | 168 | 178 | 166 | 176 | 176 | 162 | 162 | 156 | Max decrease 10% (for all class of Voltage) | 165 | 38.99 | 167 | 160 | 172 | 159 | 152
Remarks |  |  | Send bottom oil sample again & follow the sampling guidelines. |  |  | The test results of 28.10.02 when compared with the previous test results i.e. on 18.9.02 indicatesvariation in Resistivity, Tan-Delta & Flash Point. As such you are requested to send one more oil sample duly observing sampling guidelines. |  | Send oil sample again duly observing sampling guidelines. | Send oil sample again duly observing sampling guidelines. | Flash Point test is not carried out due to Equipment fault. |  | DGA not carriedout due to Equipment fault. Send oil sample again as per the sampling guidelines. | See Note 2(Filtration) Send oil sample again AFTER FILTRATION as per the sampling guidelines enclosed. Flash Point test is not carriedout due to Equipment fault. | Filtration was recommended during Mar -05. Please clarify whether the filtration is carriedout or not. | Flashpoint test was not carried out due to equipment fault. |  | Send oil sample again as per the sampling guidelines. Furnish Last date of Filtration. In the ltr cited under ref. the DOC is mentioned as 1.7.96 but in this office records DOC is 18.10.96. clarify which is correct. | Send oil sample again within a month | Due to urgency DGA is not carried out. Send oil sample again within 15 days. |  |  |  | Send oil sample again within one month. |  | Furnish IR & PI Values. | The gases evolved are within permissible limits. |  |  | Send sample again within a month. | Send oil sample again after a month for DGA | Send oil sample again within a month. Furnish IR & PI value( IR @10 min to 1 min ratio.) | Strictly foolow note 2. and send oil sample again after 3 months for testing. | Send oil sample again after filtration. Filtration should be carried out in dry weather condition after arresting the oil leakages if any. |  |  |  |  | Resistivity |  | Sampling error suspected. |  | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 31 | 15 | 34 | 14 | 12 | 16 | 17 | 15 | 20 | 12 | 12 | 19 | 14 | 7 | 29 | 19 | 12 | 20 | 19 | 15 | 20 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 22 | 24 | 25 | 23 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 20 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 |  | 12 | 20 | 25 | 16 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) |  |  | 5 | 15 | 10 | 12 | 11 | 5 | 9 | 20 | 9 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 11 | 19 | 13 | 49 | 20 | 25 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | [7 empty] | 44 | 24 | 53 | 11 | 25 | 34 | 35 | 16 | 24 | 20 | 17 | 25 | 9 | 25 | 21 | 58 | 40 | 35 | 29 | 15 | 28 | 29 | 36 | 31 | 32 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 14 | 24 | 14 | 32 | 33 | 25 | 30
[42 empty] | Remarks |  | Send oil sample again as per the sampling guidelines enclosed. Furnish Date of Commission & Last date of Filtration. | In T.O. previous record the transformer sl no is 13158 where as in your ltr cited under ref. it is mentioned as 13185. Please confirm which is correct. FURNISH DATE OF COMMISSION & LAST DATE OF FILTRATION. | In Jan 2005 you were requested to clarify the sl no of the transformer. But so far you have not clarified the correct sl no of the transformer. Please furnish correct sl no of the transformer. | Earlier the Tr.SL No was furnished as 13158 but now it is given as 13185, so please clarify the correct sl No. See DGA report . | See DGA Report.when compared previous test result there is variation in respect of item no 2 & 3. |  |  |  |  | Flash Point test is not carried out due to Equipmetn fault. See DGA Report. |  |  |  | When compared with the previous test report there is variation in respect of Resistivity and Tan-delta. Clarify whether the oil is been topped up. If topped up furnish the date and quantiy of oil and whether the oil is filterrred before topping up. The value of flash point ishas reduced. | Oil may be filtered before filling into the transformer. | [5 empty] | Compared to previous test results there is a variation in resistivity and tan delta values. clarify whether the oil is topped up. | [5 empty] | Remarks | [8 empty] | Remarks |  |  | Send bottom oil sample again & follow sampling guidelines. |  |  | When compared to previous test results there is variation in respect of Resistivity and Tan-Delta. Flash Point test is not carried out due to Equipment fault. DGA is carried out due to insufficient evolution of Gas. | DGA Not carried out due to insufficient evolution og gases. | [8 empty] | Compared to previous test results there is variation in resistivity and tan delta values. |  |  |  | Remarks | [8 empty] | Send oil sample again as per the sampling guidelines enclosed. Furnish Date of Commission & Last date of Filtration. DGA is not carriedout due to Equipment fault. | Send oil sample again as per the sampling guidelines enclosed. FURNISH DATE OF COMMISSION & LAST DATE OF FILTRATION. | See Note 2 (Filtration). Send oil sample again AFTER FILTRATION as per the sampling guidelines enclosed. Flash Point test is not carriedout due to Equipment fault. | Flash Point test is not carriedout due to Equipment fault. DGA is not carriedout due to insufficient evolution of Gas. | Moisture still persists even after filteration.Send oil sample again as per the sampling guidelines. | Send oil sample again as per the sampling guidelines. | Moisture still persists in the oil.Send oil sample again as per the sampling guidelines. |  | Send oil sample again as per the sampling guidelines. Flash point test is not carried out diue to equipment fault. |  |  |  |  | Send oil sample again within a month. | Furnish last date of filtration. Test for IR & PI values & furnish the same to this office for further recommendation.Check for oil leakages & arrest the same. | Furnish IR and PI Values. Send oil sample again within a month. The gases are within limits. | Send oil sample again within a month. Furnish IR & PI Values, | Send oil sample after filtration.Filtration should be carried out in dry weather and after arresting the oil leakage if any. | Send oil sample again for testing. |  | Send oil sample again within a month. |  | Send sample again within 2 month.Due care shall be taken while sampling. |  | 1)Drain out the oil completely. 2) Remove sludge at the bottom of the Transformer 3) Hot air circulation till the PI values are satisfactory. 4)Overhaul the transformer by replacing the Rubber gaskets/cocksheets etc. 5. Filter the oil, inconsultation with RT | [6 empty] | Sampling error suspected.

## 220KV MALUR
Name Of Station : Malur 220kV |  | Capacity : 100MVA |  |  | Serial Number : T-1035/03 | [34 empty] | Name Of Station : Malur 220kV |  | Capacity : 100MVA |  |  | Serial Number : 13024-002
SSMD : Malur |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 23-Sep-99 | [34 empty] | SSMD : Malur |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 10-Mar-06
Zone : BANGALORE |  | Make : APEX |  |  | YOM : 1998 | [34 empty] | Zone : BANGALORE |  | Make : ABB |  |  | YOM : 2005
| Permissible limits as per IS 1866:2000 | [31 empty] | Permissible limits as per 1866-2017 | [7 empty] | Permissible limits as per IS 1866:2000 | [17 empty] | Permissible limits as per 1866-2017
Last Filtn. Date |  | 1999 | 1999 | 1999 | 1999 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2016 | 2016 | 2016 | 2016 | 2016 |  | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | Last Filtn. Date |  | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 | 2006 |  | 2006 | 2006 | 2006 | 2006
Sampling Date | [39 empty] | Sampling Date
Date of Test | Permissible limits as per IS 1866:2000 | 2000-05-24 | 2001-04-10 | 2001-09-27 | 2002-05-15 | 2002-07-19 | 2002-08-30 | 2002-10-18 | 2003-04-24 | 2004-03-30 | 2005-03-05 | 2005-07-15 | 2006-08-22 | 2006-11-07 | 2007-11-07 | 2008-06-06 | 2008-11-07 | 2009-06-29 | 2009-08-14 | 2010-07-20 | 2012-01-10 | 2013-01-04 | 2014-03-19 | 2014-08-11 | 2015-08-11 | 2016-03-23 | 2016-05-25 | 2016-05-26 | 2017-07-10 | 2017-12-14 | 2020-08-20 | Vol Class Good Fair Poor | 2021-09-18 | 2022-06-07 | 2022-06-21 | 2022-10-01 | 2023-12-11 | 2024-12-23 | 2026-05-30 | Date of Test | Permissible limits as per IS 1866:2000 | 2006-08-19 | 2007-11-07 | 2008-06-04 | 2009-06-29 | 2010-07-22 | 2012-01-09 | 2013-01-04 | 2014-03-19 | 2014-08-11 | 2015-08-11 | 2016-06-17 | 2016-08-30 | 2017-07-07 | 2017-12-14 | 2020-08-20 | 2020-10-14 | Vol Class Good Fair Poor | 2021-09-18 | 2022-10-17 | 2023-12-11 | 2024-12-23
Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.1 |  | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.0488 | 0.0672 | 0.0527 |  | 0.0329 | 0.0355 | 0.0764 | 0.0841 | 0.0832 | 0.0524 | 0.048 | Aci dity | 0.3 mg KOH / gm(Max) | 0.006 | 0.0311 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0112 | 0.0068 | 0.0079 | 0.0037 |  | 0.0056 | 0.0169 | 0.0189 | 0.0118
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 1.41 | 6.2 |  | 11.7 | 5.4 | 4.74 | 4.82 | 3.14 | 3.5 | 2.04 | 1.95 | 1.78 | 1.58 | 1.38 | 1.1 | 1.09 | 1.04 | 1.07 | 1.06 | 0.71 | 1.81 | 0.71 | 0.75 | 0.457 | 0.455 | 0.3157 | 0.285 | 0.3062 | 0.2511 | 0.2804 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 2.8 | 2.8 | 2.6 | 2.8 | 0.088 | 3.3 | 2.8 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 93.8 | 90.4 | 173 | 161 | 109 | 103 | 75.9 | 176.7 | 175.6 | 80.64 | 122.7 | 140.8 | 139.4 | 120.5 | 112.19 | 128.7 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 840 | 1080 | 680 | 630
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.025 | 0.0082 |  | 0.003 | 0.006 | 0.007 | 0.008 | 0.0139 | 0.0134 | 0.0142 | 0.016 | 0.02 | 0.025 | 0.0181 | 0.02 | 0.022 | 0.024 | 0.023 | 0.024 | 0.028 | 0.021 | 0.028 | 0.03 | 0.064 | 0.0657 | 0.0541 | 0.0611 | 0.0488 | 0.0615 | 0.0682 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.0601 | 0.0618 | 0.064 | 0.0575 | 1.82 | 0.0826 | 0.0157 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0006 | 0.0014 | 0.0003 | 0.0004 | 0.0004 | 0.0006 | 0.00108 | 0.0017 | 0.0018 | 0.0025 | 0.00129 | 0.00012 | 0.00022 | 0.00026 | 0.00085 | 0.00039 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.00047 | 0.00084 | 0.00072 | 0.00061
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 56 | 32 |  | 66 | 93 | 78 | 67 | 92 | 77 | 84 | 64 | 53 | 65 | 45 | 45 | 66 | 64 |  | 67 | 59 | 57 | 55 |  |  |  | 61 | 67 |  |  | 42 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 28 | 28 | 55 | 88 | 36 | 57 |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 61 | 44 | 70 | 62 | 54 | 70 | 54 | 25 | [6 empty] | 44 |  | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 56 | 57 | 96 | 63
BDV (B) |  | 26 | 22 |  | 20 | 84 | 75 | 66 | 88 | 58 | 51 | 50 | 44 | 58 | 26 | 34 | 65 | 41 | 68 | 50 | 50 | 50 |  | 32 | 40 | 42 | 54 | 65 | 49 | 57 | 33 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 25 | 22 | 50 | 42 | 23 | 41 | 23 | BDV (B) |  | 36 | 32 | 50 | 61 | 50 | 56 | 51 |  | 52 | 58 | 38 | 56 | 77 | 70 | 35 | 49 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 53 | 48 | 34 | 60
IFT | 15 Dynes / cm (Min) | 30 | 30 |  | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 25 | 25 | 20 | 20 | 20 | 20 | 20 | 14.9 | 14.31 | 14.04 | >25 20-25 <20 (for all voltage class) | 15.11 | 15 | 18.52 | 17.98 | 15.61 | 14.62 | 14.96 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 40.37 | 39.04 | 44.24 | 34.89 | >25 20-25 <20 (for all voltage class) | 35.53 | 36.1 | 32.52 | 34.65
F P | 125° C (Min) |  |  |  | 171 | 176 | 176 | 176 | 176 | 175 | 175 |  |  |  | 169 | 169 |  |  | 175 | 175 | 173 | 169 | 170 | 169 | 166 | 161 | 170 | 170 | 176 | 170 | 170 | Max decrease 10% (for all class of Voltage) | 178 | 159 | 168 | 167 | 167 | 163 | 165 | F P | 125° C (Min) |  | 151 |  |  | 169 | 169 | 167 | 168 | 167 | 166 | 153 | 156 | 176 | 170 | 158 | 156 | Max decrease 10% (for all class of Voltage) | 11 | 166 | 162 | 164
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) |  |  |  | 31 | 10 |  |  | 11.5 | 14 | 13 | 16 | 19 | 20 | 17 | 17 | 12 | 13 | 12 | 16 | 20 | 16 | 26 | 22 | 33 | 28 | 20 | 13 | 34 | 30 | 24 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 31 | 36 | 29 | 29 | 44 | 46 | 76 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 13 | 33 | 10 | 6 | 15 | 6 | 15 | 19 | 10 | 20 | 6 | 12 | 8 | 9 | 5 | 15 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 4 | 20 | 26 | 14
Remarks |  |  | Send the bottom oil sample again & follow the sampling guidelines. |  | Send oil sample again & follow the sampling guidelines. | [6 empty] | Flash Point test is not carriedout due to Equipment fault. | Send oil sample again as per the sampling guidelines. |  | Sampling error is suspected. Send oil sample again as per the sampling guidelines. | Since BDV value is poor send oil sample again as per the sampling guidelines.Due care shall be taken while sampling. | Flash Point test is not carried out due to equipment fault. | Furnish YOM. | Furnish YOM & last date of filtration. |  | Furnish YOM. | As per our records the date of filtration is 2002.Furnish the latest date of filtration if any.Send oil sample for DGA after 6-8 months. |  | Filter the oil & send sample for testing. Furnish IR & PI values & also last date of filtration. Check for loose gaskets & oil leakage & arrest if any. | The gases evolved are within limits. It is observed from the results that either the oil is not filtered or the sampling is not proper. Clarify | It was mentioned to filter the oil in the prev reports.But till date the filtration has not been carried out. Filter oil without fail and send sample again for testing. | Filtration may be continued to improve BDV & Water content. |  | Send oil sample again within a month. See Note 2 | Send sample again within a minth. See note 2. Furnish IR & Pi value. | Strictly follow note 2 |  | Check for IR & PI ( IR @10min/1min ratio) and furnish the results. | [6 empty] | Remarks |  | Send oil sample again as per the sampling guidelines.Care sall be taken while sampling.DGA not carried out due to insufficient evolution of Gas | Care shall be taken while sampling. Send oil sample again as per the sampling guidelines. |  | Furnish YOM. |  |  | When compared to previous test results, there is variation in the value of Resistivity and Tan-Delta.(The value of Rsisitivity has reduced from 103 to 75.9, and value of tan-delta has increased from 0.0006 to 0.00108). Clarify. |  |  | The gases are within limits | Send oil sample again within a month. |  | Send oil sample again after a month for DGA |  | Suspected sampling error ,re send the oil duly following the sampling guidelines | Sampling error suspected.

## 220KV NRS RAJAJINAGAR
Name Of Station : NRS Rajajinagar |  | Capacity : 100MVA |  |  | Serial Number : 6800000168 | [21 empty] | Name Of Station : NRS Rajajinagar |  | Capacity : 20MVA |  |  | Serial Number : 2800055501 | [17 empty] | Name Of Station : NRS Rajajinagar |  | Capacity : 20MVA |  |  | Serial Number : 2800055500 | [18 empty] | Name Of Station : NRS Rajajinagar |  | Capacity : 20MVA |  |  | Serial Number : 2800056329 | [17 empty] | Name Of Station : NRS Rajajinagar |  |  |  | Serial Number : 13044-005
SSMD : NRS |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 05-Jun-98 | [21 empty] | SSMD : NRS |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 31-Oct-95 | [17 empty] | SSMD : NRS |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 05-Jul-98 | [18 empty] | SSMD : NRS |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 01-Jan-98 | [17 empty] | SSMD : NRS |  |  |  | Date Of Commission : 18-Oct-07
Zone : BANGALORE |  | Make : NGEF |  |  | YOM : 1997 | [21 empty] | Zone : BANGALORE |  | Make : NGEF |  |  | YOM : 1995 | [17 empty] | Zone : BANGALORE |  | Make : NGEF |  |  | YOM : 1995 | [18 empty] | Zone : BANGALORE |  | Make : NGEF |  |  | YOM : 1997 | [17 empty] | Zone : BANGALORE |  |  |  | YOM : 2007
| Permissible limits as per IS 1866:2000 | [20 empty] | Permissible limits as per 1866-2017 | [5 empty] | Permissible limits as per IS 1866:2000 | [17 empty] | Permissible limits as per 1866-2017 |  |  |  |  | Permissible limits as per IS 1866:2000 | [18 empty] | Permissible limits as per 1866-2017 |  |  |  |  | Permissible limits as per IS 1866:2000 | [16 empty] | Permissible limits as per 1866-2017 | [5 empty] | Permissible limits as per IS 1866:2000 | [12 empty] | Permissible limits as per 1866-2017
Last Filtn. Date |  | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 |  | 1998 | 1998 | 1998 | 1998 | 1998 | Last Filtn. Date |  | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 |  | 1998 | 1998 | 1998 | 1998 | Last Filtn. Date |  | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 |  | 1998 | 1998 | 1998 | 1998 | Last Filtn. Date |  | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 1998 | 2013 | 2013 | 2013 | 2013 | 2018 | 2018 |  | 2018 | 2018 | 2018 | 2018 | 2018 | Last Filtn. Date |  | 2006 | 2006 | 2006 | 2006 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 |  | 2016 | 2016 | 2016 | 2016
Sampling Date | [26 empty] | Sampling Date | [22 empty] | Sampling Date | [23 empty] | Sampling Date | [22 empty] | Sampling Date
Date of Test | Permissible limits as per IS 1866:2000 | 2001-09-06 | 2002-02-19 | 2002-10-26 | 2005-03-21 | 2006-04-21 | 2008-03-03 | 2008-09-25 | 2008-10-31 | 2009-09-30 | 2010-11-25 | 2011-10-12 | 2013-10-25 | 2016-02-11 | 2016-06-22 | 2016-11-07 | 2017-11-17 | 2019-11-04 | 2019-11-07 | 2020-07-28 | Vol Class Good Fair Poor | 2020-10-16 | 2022-02-21 | 2023-06-01 | 2024-02-28 | 2025-03-11 | Date of Test | Permissible limits as per IS 1866:2000 | 2001-09-06 | 2002-02-08 | 2005-06-22 | 2006-04-03 | 2008-01-28 | 2009-09-30 | 2010-11-23 | 2011-10-22 | 2013-07-08 | 2013-07-10 | 2016-02-23 | 2016-11-24 | 2017-01-17 | 2017-11-17 | 2019-11-07 | 2020-10-16 | Vol Class Good Fair Poor | 2022-02-01 | 2023-03-09 | 2024-02-28 | 2025-03-11 | Date of Test | Permissible limits as per IS 1866:2000 | 1997-09-02 | 1998-09-29 | 2000-03-10 | 2001-09-06 | 2002-02-08 | 2005-06-23 | 2006-04-03 | 2008-01-24 | 2009-09-15 | 2010-11-23 | 2011-10-22 | 2013-02-28 | 2016-02-23 | 2016-11-24 | 2017-11-17 | 2019-11-07 | 2020-10-16 | Vol Class Good Fair Poor | 2022-02-01 | 2023-03-09 | 2024-02-28 | 2025-03-11 | Date of Test | Permissible limits as per IS 1866:2000 | 2002-02-08 | 2005-06-22 | 2006-04-03 | 2008-02-29 | 2009-09-15 | 2010-11-23 | 2011-10-22 | 2013-02-28 | 2013-03-23 | 2013-04-17 | 2016-02-23 | 2016-11-24 | 2017-11-17 | 2019-11-07 | 2020-10-16 | Vol Class Good Fair Poor | 2022-01-29 | 2023-03-09 | 2024-02-28 | 2024-08-26 | 2025-03-11 | Date of Test | Permissible limits as per IS 1866:2000 | 2009-09-30 | 2010-11-25 | 2011-10-12 | 2013-10-23 | 2016-02-11 | 2016-11-07 | 2016-11-28 | 2016-12-02 | 2017-11-17 | 2019-11-07 | 2020-10-16 | Vol Class Good Fair Poor | 2022-02-21 | 2023-05-29 | 2024-02-28 | 2025-03-11
Aci dity | 0.3 mg KOH / gm(Max) | 0.1 | 0.05 | 0.05 | 0.05 | 0.013 | 0.02 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.0099 | 0.0098 | 0.0176 | 0.0144 |  | 0.0132 | 0.0519 | 0.0684 | 0.0279 | 0.068 | Aci dity | 0.3 mg KOH / gm(Max) | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.05 | 0.0884 | 0.1845 | 0.0886 |  | 0.0891 | 0.0709 | 0.058 | 0.08 | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.038 | 0.14 | 0.078 |  | 0.0921 | 0.0206 | 0.0688 | 0.071 | Aci dity | 0.3 mg KOH / gm(Max) | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3 | 0.2 | 0.1214 | 0.1212 | 0.1429 |  | 0.16 | 0.0612 | 0.0671 | 0.0054 | 0.068 | Aci dity | 0.3 mg KOH / gm(Max) | 0.013 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0098 | 0.116 | 0.0062 |  | 0.0058 | 0.0151 | 0.0181 | 0.012
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 0.81 | 2.15 | 2.65 | 6.26 | 5.83 | 8.33 | 8.79 | 9.91 | 9.94 | 8.1 | 9.89 | 9.73 | 5.589 | 5.46 | 7.737 | 4.181 | 14.074 | 3.13 | 4.244 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 5.616 | 24 | 20 | 11 | 10.2 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 1.25 | 0.709 | 0.768 | 0.704 | 0.82 | 0.818 | 0.531 | 0.524 | 0.651 | 0.585 | 0.4093 | 0.274 | 33.15 | 0.4423 | 0.7266 | 0.7238 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 7 | 8 | 8 | 10 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 2.98 | 5.07 | 1.51 | 1.18 | 0.737 | 0.668 | 0.537 | 0.402 | 0.407 | 0.528 | 0.487 | 0.559 | 0.6045 | 0.4969 | 0.347 | 0.6063 | 0.5716 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 4.37 | 7.5 | 7 | 4.99 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 1.03 | 0.331 | 0.318 | 0.269 | 0.273 | 0.211 | 0.214 | 0.209 | 0.179 | 0.234 | 0.1886 | 0.226 | 0.1317 | 0.1205 | 0.3961 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 1.3 | 1.07 | 1.5 | 1.5 | 1.49 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 86.3 | 84.1 | 57.3 | 57 | 41.29 | 49.58 | 38.11 | 44.11 | 43.05 | 50.86 | 79.17 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 550 | 480 | 480 | 409
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0282 | 0.024 | 0.031 | 0.0092 | 0.011 | 0.0078 | 0.014 | 0.0081 | 0.0079 | 0.011 | 0.0007 | 0.0007 | 0.0294 | 0.0289 | 0.00741 | 0.01345 | 0.02183 | 0.01545 | 0.0214 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.0197 | 0.0338 | 0.0266 | 0.0354 | 0.039 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0194 | 0.037 | 0.0395 | 0.043 | 0.028 | 0.029 | 0.041 | 0.043 | 0.025 | 0.034 | 0.0512 | 0.025 | 0.0619 | 0.043 | 0.475 | 0.0397 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.0208 | 0.03044 | 0.0224 | 0.025 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0094 | 0.004 | 0.018 | 0.0184 | 0.037 | 0.038 | 0.047 | 0.052 | 0.051 | 0.042 | 0.053 | 0.042 | 0.0493 | 0.0301 | 0.0609 | 0.0429 | 0.0531 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.03758 | 0.033 | 0.02689 | 0.0366 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.029 | 0.069 | 0.058 | 0.082 | 0.079 | 0.085 | 0.018 | 0.089 | 0.098 | 0.085 | 0.1472 | 0.599 | 0.1656 | 0.207 | 0.198 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.113 | 0.1439 | 0.1255 | 0.154 | 0.197 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0004 | 0.0004 | 0.0008 | 0.0008 | 0.00243 | 0.00204 | 0.0023 | 0.00188 | 0.00034 | 0.00199 | 0.00391 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.00062 | 0.00112 | 0.001498 | 0.00183
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 2005-03-21: 92; 2006-04-21: 94; 2008-03-03: 79; 2013-10-25: 76; 2019-11-07: 85 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 60 | 75 | 45 | 87 | 65 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  |  | 63 | [11 empty] | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  |  |  |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [7 empty] | 60 |  |  |  | 74 | [5 empty] | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  |  |  |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [7 empty] | 43 | 52 | [6 empty] | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | [5 empty] | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [9 empty] | 95 | 96 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 60 | 23 | 35 | 40
BDV (B) |  | 62 | 16 | 89 | 61 | 78 | 23 | 36 | 56 | 55 | 63 | 78 | 69 | 96 | 58 | 57 | 43 | 74 | 83 | 65 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 67 | 53 | 27 | 91 | 55 | BDV (B) |  | 83 | 56 | 70 | 48 | 30 | 32 | 34 | 40 | 75 | 75 | 53 | 45 | 65 | 35 | 44 | 42 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 40 | 50 | 34 | 48 | BDV (B) |  | 36 | 37 | 36 | 24 | 88 | 64 | 59 | 31 | 53 | 37 | 39 | 64 | 34 | 79 | 72 | 69 | 53 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 34 | 69 | 39 | 43 | BDV (B) |  | 37 | 90 | 96 | 82 | 63 | 40 | 46 | 42 | 36 | 68 | 42 | 49 | 67 | 58 | 90 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 69 | 77 | 61 | 47 | 30 | BDV (B) |  | 42 | 50 | 52 | 41 | 71 | 37 | 59 | 68 | 52 | 92 | 52 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 35 | 22 | 27 | 26
IFT | 15 Dynes / cm (Min) | 35 | 30 | 35 | 35 | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 30 | 34.56 | 32.14 | 31.95 | 32.83 | >25 20-25 <20 (for all voltage class) | 34.82 | 25.17 | 16.54 | 19.42 | 19.85 | IFT | 15 Dynes / cm (Min) | 30 | 30 | 30 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 35 | 14.99 | 14.32 | 17.46 | >25 20-25 <20 (for all voltage class) | 18.57 | 19.75 | 17.14 | 14.69 | IFT | 15 Dynes / cm (Min) | 25 | 25 | 30 | 30 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 14.27 | 15.17 | 20.61 | >25 20-25 <20 (for all voltage class) | 19.76 | 25.8 | 18.64 | 17.44 | IFT | 15 Dynes / cm (Min) | 30 | 30 | 30 | 25 | 25 | 20 | 20 | 20 | 20 | 20 | 15 | 20 | 9.37 | 16.13 | 13.79 | >25 20-25 <20 (for all voltage class) | 10.13 | 16.47 | 16.94 | 10.64 | 11.85 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 38.3 | 32.25 | 35.6 | >25 20-25 <20 (for all voltage class) | 31.52 | 31.65 | 34.17 | 33.26
F P | 125° C (Min) |  | 161 | 168 | [5 empty] | 169 | 169 | 177 | 175 | 171 | 168 | 167 | 161 | 164 | 165 | 167 | Max decrease 10% (for all class of Voltage) | 167 | 159 | 159 | 162 | 162 | F P | 125° C (Min) | [5 empty] | 149 | 145 | 145 | 143 | 147 | 147 | 149 | 157 | 163 | 156 | 163 | Max decrease 10% (for all class of Voltage) | 159 | 160 | 167 | 170 | F P | 125° C (Min) | [8 empty] | 175 | 143 | 153 | 151 | 145 | 149 | 159 | 168 | 165 | Max decrease 10% (for all class of Voltage) | 160 | 163 | 172 | 168 | F P | 125° C (Min) |  |  |  |  | 161 | 157 | 157 | 156 | 155 | 153 | 157 | 166 | 168 | 154 | 166 | Max decrease 10% (for all class of Voltage) | 171 | 162 | 168 | 169 | 153 | F P | 125° C (Min) | 153 | 153 | 159 | 157 | 160 | 156 | 156 | 156 | 163 | 169 | 163 | Max decrease 10% (for all class of Voltage) | 160 | 165 | 165 | 159
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) |  |  | 12 | 15 | 15 | 47 | 18 | 9 | 12 | 12 | 11 | 4 | 3 | 16 | 14 | 12 | 8 | 14 | 12 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 13 | 24 | 56 | 16 | 18 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) |  |  | 22 | 23 | 78 | 20 | 14 | 26 | 24 | 15 | 19 | 20 | 9 | 32 | 32 | 33 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 32 | 24 | 40 | 27 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | [5 empty] | 28 | 23 | 33 | 15 | 16 | 25 | 12 | 36 | 15 | 26 | 27 | 33 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 26 | 20 | 41 | 28 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) |  | 15 | 14 | 9 | 14 | 19 | 30 | 17 | 28 | 18 | 31 | 17 | 36 | 38 | 39 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 38 | 30 | 51 | 27 | 35 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 10 | 14 | 7 | 17 | 2 | 20 | 15 | 5 | 10 | 7 | 10 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 38 | 27 | 29 | 46
Remarks |  | 2002-02-19: Send oil sample again after two months for further evaluation & recommendation.; 2005-03-21: When compared to previous test rsults there is variation in respect of resistivity and Tan-Delta. Flash Point test is not carriedout due to Equipment fault.; 2008-03-03: Due care shall be taken while sampling . send oil ample again as per the sampling guidelines.; 2008-09-25: Send oil sample agian as per the sampling guidelines. Flash Point test is not carried out due to Equipment fault.; 2008-10-31: Flash Point test is not carried out due to Equipment fault.; 2009-09-30: Furnish last date of Filtration; 2016-02-11: The gases evolved are within limits. | [6 empty] | Remarks |  |  |  | Flash Point test is not carriedout due to Equipment fault. |  | Send oil sample again as per the sampling guidelines. Due care shall be taken while sampling. | Furnish last date of Filtration. |  | Furnish last date of filtration of the oil without fail. | [11 empty] | Sampling error suspected. |  | Remarks |  |  |  |  | Send bottom oil sample again & follow sampling guidelines. |  | Flash Point test is not carriedout due to Equipment fault. |  |  |  |  | Furnish last date of filtration. | [9 empty] | Sampling error suspected. |  | Remarks |  |  | Flash Point test is not carriedout due to Equipment fault. |  |  |  |  | Furnish last date of filtration. | [11 empty] | Sampling error suspected. |  |  | Remarks |  | Sampling error is suspected. Send oil sample again as per the sampling guidelines. |  |  |  | The gases evolved are within limits. | Send oil sample again within a month. | [6 empty] | Sampling error suspected. send oil sample again for testing.

## 220KV SARJAPURA
Name Of Station : Sarjapur |  | Capacity : 20MVA |  |  | Serial Number : 4-0049/1 | [10 empty] | Name Of Station : Sarjapur |  | Capacity : 100MVA |  |  | Serial Number : HT-1713/12775 | [27 empty] | Name Of Station : Sarjapur |  | Capacity : 100MVA |  |  | Serial Number : B-30099 | [27 empty] | Name Of Station : Sarjapur |  |  |  | Capacity : 20MVA |  | Serial Number : PT-7769
SSMD : Yerandanahalli |  | Voltage Class : 66/11 KV |  |  | Date Of Commission : 29-12-2009 | [10 empty] | SSMD : Yerandanahalli |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 19-Jul-10 | [27 empty] | SSMD : Yerandanahalli |  | Voltage Class : 220/66 KV |  |  | Date Of Commission : 29-12-2009 | [27 empty] | SSMD : Yerandanahalli |  |  |  | Voltage Class : 66/11 KV |  | Date Of Commission : 04-10-2017
Zone : BANGALORE |  | Make : VICTORY |  |  | YOM : 2011 | [10 empty] | Zone : BANGALORE |  | Make : EMCO |  |  | YOM : 2007 | [27 empty] | Zone : BANGALORE |  | Make : AREVA |  |  | YOM : 2008 | [27 empty] | Zone : BANGALORE |  |  |  | Make : IMP |  | YOM : 2016
| Permissible limits as per IS 1866:2000 | [5 empty] | Permissible limits as per 1866-2017 | [9 empty] | Permissible limits as per IS 1866:2000 | [24 empty] | Permissible limits as per 1866-2017 | [7 empty] | Permissible limits as per IS 1866:2000 | [24 empty] | Permissible limits as per 1866-2017 | [7 empty] | Permissible limits as per IS 1866:2000 |  |  |  |  | Permissible limits as per 1866-2017
Last Filtn. Date |  | 2010 | 2010 | 2010 | 2010 |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | Last Filtn. Date |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 |  |  | Last Filtn. Date |  | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | 2010 | Last Filtn. Date |  | 2017 | 2017 | 2017 |  | 2017 | 2017 | 2017 | 2017 | 2017
Sampling Date | [15 empty] | Sampling Date | [32 empty] | Sampling Date | [32 empty] | Sampling Date
Date of Test | Permissible limits as per IS 1866:2000 | 2014-01-25 | 2015-10-17 | 2017-02-13 | 2020-07-21 | Vol Class Good Fair Poor | 2021-08-25 | 2022-12-06 | 2023-04-26 | 2023-05-04 | 2023-05-12 | 2023-05-15 | 2023-10-17 | 2024-11-13 | 2026-04-06 | Date of Test | Permissible limits as per IS 1866:2000 | 2011-07-27 | 2012-12-21 | 2013-12-03 | 2015-03-11 | 2015-05-28 | 2016-06-17 | 2016-08-19 | 2016-10-13 | 2016-11-04 | 2017-07-24 | 2017-09-06 | 2018-02-21 | 2020-07-15 | 2016-01-14 | 2016-01-28 | 2016-01-30 | 2016-05-30 | 2016-06-04 | 2016-06-17 | 2017-07-22 | 2017-09-06 | 2020-07-15 | Vol Class Good Fair Poor |  | 2021-09-21 | 2022-09-08 | 2022-09-21 | 2022-09-22 | 2023-10-17 | 2024-11-13 | 2026-04-15 | Date of Test | Permissible limits as per IS 1866:2000 | 2011-07-07 | 2011-12-19 | 2011-12-24 | 2011-12-25 | 2011-12-26 | 2011-12-27 | 2011-12-28 | 2013-05-22 | 2013-05-23 | 2015-05-05 | 2015-07-06 | 2015-08-10 | 2015-12-16 | 2016-01-14 | 2016-01-28 | 2016-01-30 | 2016-05-30 | 2016-06-04 | 2016-06-17 | 2017-07-22 | 2017-09-06 | 2020-07-15 | Vol Class Good Fair Poor |  | 2021-07-29 | 2021-09-21 | 2022-09-08 | 2022-09-22 | 2023-10-17 | 2024-11-12 | 2026-04-15 | Date of Test | Permissible limits as per IS 1866:2000 | 2018-06-28 | 2019-05-27 | 2020-07-15 | Vol Class Good Fair Poor | 2021-07-29 | 2022-09-08 | 2023-10-17 | 2024-11-29 | 2026-11-26
Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.0053 |  | 0.0119 | 0.006 | 0.0045 |  |  |  | 0.0077 | 0.011 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 |  | 0.0098 | 0.0103 | 0.0052 | 0.0085 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0051 | 0.0211 | 0.0049 |  |  | 0.0093 | 0.0086 | 0.0098 | 0.0098 | 0.015 | 0.0095 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0051 | 0.0211 | 0.0049 |  |  | 0.0155 | 0.0182 | 0.0063 | 0.014 | 0.0189 | 0.0155 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.0028 | 0.0041 | 0.0011 |  | 0.0099 | 0.076 | 0.0188 | 0.0087 | _
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 185.6 | 201.9 | 126.9 | 168.1 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 800 | 1400 | 3000 |  |  |  | 2000 | 1700 | 720 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 82.8 | 90.1 | 89.6 | 89 | 86.3 | 65.19 | 7.58 | 75.65 | 49.57 | 129.2 | 125 | 139.4 | 134.3 | 93.13 | 46.93 | 46.93 | 47.77 | 74.54 | 65.19 | 36.017 | 39.465 | 78.36 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 |  | 620 | 700 | 880 | 880 | 860 | 849 | 565.2 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 43.1 | 83.1 | 60.1 | 62.4 | 60.9 | 63.9 | 67.1 | 2.9 | 29.4 | 24.6 | 82.27 | 141.6 | 90.49 | 93.13 | 46.93 | 46.93 | 47.77 | 74.54 | 65.19 | 36.017 | 39.465 | 78.36 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 |  | 510 | 330 | 880 | 880 | 840 | 832 | 860 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 163.2 | 118.8 | 108.1 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 870 | 1600 | 1620 | 1500 | 1400
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0006 | 0.00018 | 0.00016 | 0.00075 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.000519 | 0.000657 | 0.000463 |  |  |  | 0.000536 | 0.000971 | 0.00183 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0007 | 0.0006 | 0.0006 | 0.0006 | 0.0009 | 0.00174 | 0.00345 | 0.00031 | 0.00022 | 0.0001 | 0.00059 | 0.00026 | 0.00068 | 0.00172 | 0.00194 | 0.00194 | 0.0019 | 0.00165 | 0.00174 | 0.0019 | 0.00188 | 0.00168 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 |  | 0.001067 | 0.00852 | 0.000917 | 0.000917 | 0.00072 | 0.00071 | 0.00318 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.001 | 0.0003 | 0.0004 | 0.0006 | 0.0006 | 0.0007 | 0.0008 | 0.02 | 0.005 | 0.005 | 0.00402 | 0.00156 | 0.00196 | 0.00172 | 0.00194 | 0.00194 | 0.0019 | 0.00165 | 0.00174 | 0.0019 | 0.00188 | 0.00168 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 |  | 0.00124 | 0.001789 | 0.002106 | 0.000917 | 0.0007 | 0.00071 | 0.000926 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00016 | 0.00098 | 0.00078 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 0.00065 | 0.000491 | 0.00083 | 0.000696 | 0.000713
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  |  | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | [9 empty] | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 50 | 55 |  |  | 57 | [7 empty] | 68 |  |  |  | 64 |  |  |  |  | 62 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  | 78 | 65 | 74 | 74 | 34 | 26 | 52 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 54 | 51 |  |  |  |  | 72 |  |  |  | 87 | [5 empty] | 64 |  |  |  |  | 62 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  | 45 | 75 | 40 | 96 | 51 | 46 | 47 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 60
BDV (B) |  | 73 | 59 | 75 | 52 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 80 | 34 | 24 | 52 | 43 | 93 | 35 | 39 | 48 | BDV (B) |  | 50 | 50 | 55 | 48 | 52 | 39 | 66 | 55 | 56 | 45 | 50 | 57 | 57 | 62 | 50 | 47 | 54 | 27 | 59 | 78 | 50 | 55 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 76 | 54 | 66 | 66 | 25 | 34 | 58 | BDV (B) |  | 50 | 44 | 62 | 72 | 58 | 71 | 62 | 46 | 48 | 64 | 77 | 61 | 67 | 62 | 50 | 47 | 54 | 27 | 59 | 78 | 50 | 55 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 24 | 72 | 22 | 89 | 46 | 17 | 14 | BDV (B) |  | 53 | 45 | 56 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 48 | 37 | 46 | 70
IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 37.13 | >25 20-25 <20 (for all voltage class) | 34.67 | 34.7 | 31.81 |  |  |  | 39.15 | 33.58 | 35.91 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 37.69 | 37.22 | 37.99 | 37.96 | 35 | 35 | 30 | 30 | 35 | 35 | 39.25 | 34.81 | 38.2 | >25 20-25 <20 (for all voltage class) |  | 31.82 | 37.15 | 35.84 | 35.84 | 37.82 | 32.26 | 34.97 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 25 | 35 | 35 | 38 | 35 | 35 | 35 | 35 | 30 | 30 | 35 | 35 | 39.25 | 34.81 | 38.2 | >25 20-25 <20 (for all voltage class) |  | 34.74 | 33.25 | 36.06 | 34.82 | 34.98 | 30.52 | 26.63 | IFT | 15 Dynes / cm (Min) | 45.69 | 41.45 | 40.12 | >25 20-25 <20 (for all voltage class) | 32.7 | 33.82 | 37.41 | 38.16 | 37.08
F P | 125° C (Min) | 159 | 157 | 165 | 158 | Max decrease 10% (for all class of Voltage) | 173 | 166 | 149 |  |  |  | 152 | 152 | 164 | F P | 125° C (Min) | 155 | 155 | 156 | 155 | 156 | 152 | 147 | 152 |  | 158 | 153 | 165 | 172 | 161 | 176 | 176 | 154 | 170 | 152 | 176 | 158 | 172 | Max decrease 10% (for all class of Voltage) |  | 168 | 163 | 159 | 159 | 170 | 166 | 154 | F P | 125° C (Min) | 161 | [6 empty] | 173 | 161 | 161 | 153 | 150 | 161 | 161 | 176 | 176 | 154 | 170 | 152 | 176 | 158 | 172 | Max decrease 10% (for all class of Voltage) |  | 170 | 158 | 159 | 161 | 161 | 159 | 161 | F P | 125° C (Min) | 149 | 159 | 170 | Max decrease 10% (for all class of Voltage) | 176 | 160 | 165 | 161 | 170
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 6 | 17 | 7 | 12 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 11 | 30 | 39 | 15 | 21 | 12 | 24 | 56 | 12 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 20 | 10 | 13 | 8 | 14 | 13 | 14 | 9 | 17 | 12 | 24 | 6 | 12 | 14 | 2 | 32 | 12 | 17 | 13 | 10 | 20 |  | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 |  | 12 | 25 | 15 | 15 | 29 | 31 | 7 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 20 | 8 | 119 | 17 | 17 | 16 | 5 | 37 | 5 | 6 | 10 | 13 | 11 | 14 | 2 | 32 | 12 | 17 | 13 | 10 | 20 |  | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 |  | 26 | 9 | 38 | 17 | 20 | 31 | 56 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 7 | 11 | 12 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 10 | 20 | 23 | 21 | 11
Remarks | [8 empty] | Released good Transformer diverted from 66kV Konadasapura (10-Oct-12) | [5 empty] | Variation in resistivity. | Remarks |  |  |  |  | Send oil sample again within a month | DGA shows gases are within the limits. | Send oil sample again within a month. | When compared to previous test results there is variation inrespect of Tan -delta resisitivity values. Send oil sample again for testing. |  |  | Send oil sample again within a month | Send oil sample again within a for DGA. |  |  |  | The gases evolved are within limits. | The gases evolved are within limits. |  | Send oil sample again for testing. |  | Send oil sample again after a month for DGA | Send oil sample again within a month for DGA. | [10 empty] | Remarks |  |  |  | The Filtration may be continued 4-5 cycles. |  |  |  | Send oil again after 1-2 months for DGA. | The oil sample submitted is very poor quality and is not suitable for use in 100MVA transformer(B-30099). Send oil sample of oil available in the 100MVA transformer for testing along with the oil to be topped up. | Report sent in Ltr. |  |  | Gases are within the permissible limits. |  |  | The gases evolved are within limits. | The gases evolved are within limits. |  | Send oil sample again for testing. |  | Send oil sample again after a month for DGA | Send oil sample again within a month for DGA. | [10 empty] | Remarks

## 400KV DHP
Name Of Station : 400kV Devanahalli Hardware Park |  | Capacity : 500MVA |  |  |  | Serial Number : 14104-1 |  | Name Of Station : 400kV Devanahalli Hardware Park |  | Capacity : 500MVA |  | Serial Number : 14081-01 |  |  |  |  | Name Of Station : 400kV Devanahalli Hardware Park |  | Capacity : 500MVA |  |  | Serial Number : 14081-02
SSMD : Hebbal |  | Voltage Class : 400/220 KV |  |  |  | Date Of Commission : 31-Mar-23 |  | SSMD : Hebbal |  | Voltage Class : 400/220 KV |  | Date Of Commission : 24-Sep-20 |  |  |  |  | SSMD : Hebbal |  | Voltage Class : 400/220 KV |  |  | Date Of Commission : 24-Sep-20
Zone : BANGALORE |  | Make : ABB |  |  |  | YOM : 2022 |  | Zone : BANGALORE |  | Make : ABB |  | YOM : 2019 |  |  |  |  | Zone : BANGALORE |  | Make : ABB |  |  | YOM : 2019
[9 empty] | Permissible limits as per IS 1866:2000 | [8 empty] | Permissible limits as per IS 1866:2000
Last Filtn. Date | Permissible limits as per 1866-2017 |  | 2023 | 2023 | 2023 | 2023 | 2023 | Last Filtn. Date |  | 2020 | Permissible limits as per 1866-2017 | 2020 | 2020 | 2020 | 2020 | 2020 | Last Filtn. Date |  | 2020 | 2020 | Permissible limits as per 1866-2017 |  | 2020 | 2020 | 2020 | 2020 | 2020 | 2020
Sampling Date | [7 empty] | Sampling Date | [8 empty] | Sampling Date
Date of Test | Vol Class Good Fair Poor |  | 2022-12-15 | 2023-12-19 | 2023-12-20 | 2024-09-25 | 2026-03-05 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-09-29 | Vol Class Good Fair Poor | 2021-08-03 | 2022-07-19 | 2023-09-06 | 2024-09-25 | 2026-03-05 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-09-29 | 2020-11-06 | Vol Class Good Fair Poor |  | 2021-08-03 | 2022-07-19 | 2022-12-15 | 2023-09-06 | 2024-09-25 | 2026-03-05
Aci dity | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 |  | 0.0059 | 0.0082 | 0.0082 | 0.0048 | 0.0068 | Aci dity | 0.3 mg KOH / gm(Max) | 0.0082 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0042 | 0.0088 | 0.0085 | 0.0071 | 0.0095 | Aci dity | 0.3 mg KOH / gm(Max) | 0.0089 | 0.0073 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 |  | 0.0025 | 0.0094 |  | 0.0094 | 0.006 | -
Resis tivity | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 |  | 2047 | 1670 | 1670 | 1800 | 900 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 144.6 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 910 | 1000 | 1300 | 1341 | 2300 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 168.4 | 196.5 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 |  | 1329 | 2100 |  | 2500 | 1900 | 2800
Tan - Delta | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  | 0.00095 | 0.000786 | 0.000786 | 0.00085 | 0.000359 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0003 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00049 | 0.000525 | 0.000541 | 0.00091 | 0.00156 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00042 | 0.0003 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 |  | 0.00115 | 0.00048 |  | 0.000416 | 0.00079 | 0.00064
BDV (T) | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 84 | 84 | 84 | 70 | 92 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 59 | 48 | 67 | 63 | 76 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 |  | 58 | 51 | 92 | 71 | 61 | 98
BDV (B) |  |  | 83 | 72 | 72 | 53 | 86 | BDV (B) |  | 80 |  | 51 | 46 | 66 | 57 | 96 | BDV (B) |  | 97 | 48 |  |  | 52 | 48 | 83 | 68 | 53 | 97
IFT | >25 20-25 <20 (for all voltage class) |  | 42.85 | 35.47 | 35.47 | 36.84 | 38.51 | IFT | 15 Dynes / cm (Min) | 35.18 | >25 20-25 <20 (for all voltage class) | 36.11 | 36.14 | 37.65 | 37.48 | 38.51 | IFT | 15 Dynes / cm (Min) | 36.29 | 37.23 | >25 20-25 <20 (for all voltage class) |  | 32.76 | 35.49 |  | 38.64 | 38.46 | 39.36
F P | Max decrease 10% (for all class of Voltage) |  | 164 | 161 | 161 | 166 | 154 | F P | 125° C (Min) | 171 | Max decrease 10% (for all class of Voltage) | 162 | 167 | 166 | 154 | 165 | F P | 125° C (Min) | 162 | 168 | Max decrease 10% (for all class of Voltage) |  | 171 | 169 |  | 161 | 163 | 155
ppm | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 |  | 4 | 4 | 4 | 31 | 4 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 10 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 12 | 21 | 9 | 10 | 5 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 7 | 5 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 |  | 13 | 14 | 12 | 10 | 20 | 7
Remarks | [7 empty] | Remarks | [8 empty] | Remarks |  |  | Send sample again after 2 month.

## 400KV HOODY
Name Of Station : Hoody 400kV |  | Capacity : 167MVA |  |  | Serial Number : B-30634 | [9 empty] | Name Of Station : Hoody 400kV |  | Capacity : 167MVA |  |  | Serial Number : B-30635 | [6 empty] | Name Of Station : Hoody 400kV |  | Capacity : 167MVA |  | Serial Number : B-31107 |  |  |  | Name Of Station : Hoody 400kV |  | Capacity : 167MVA |  |  | Serial Number : B-30636 | [9 empty] | Name Of Station : Hoody 400kV |  | Capacity : 167MVA |  |  | Serial Number : B-30637 | [5 empty] | Name Of Station : Hoody 400kV |  | Capacity : 167MVA |  |  | Serial Number : B-31038 | [8 empty] | Name Of Station : Hoody 400kV |  | Capacity : 167MVA |  |  | Serial Number : T8907/2 | [28 empty] | Name Of Station : Hoody 400kV |  | Capacity : 167MVA |  |  | Serial Number : T8386/3 | [26 empty] | Name Of Station : Hoody 400kV |  | Capacity : 167.5MVA |  |  | Serial Number : T8386/4
SSMD : Hoody |  | Voltage Class : 400/220 KV |  |  | Date Of Commission : 24-Jan-15 | [9 empty] | SSMD : Hoody |  | Voltage Class : 400/220 KV |  |  | Date Of Commission : 24-Jan-15 | [6 empty] | SSMD : Hoody |  | Voltage Class : 400/200 KV |  | Date Of Commission : 14-Apr-18 |  |  |  | SSMD : Hoody |  | Voltage Class : 400/220 KV |  |  | Date Of Commission : 24-Jan-15 | [9 empty] | SSMD : Hoody |  | Voltage Class : 400/220 KV |  |  | Date Of Commission : 27-Jan-15 | [5 empty] | SSMD : Hoody |  | Voltage Class : 400/220 KV |  |  | Date Of Commission : 08-Oct-16 | [8 empty] | SSMD : Hoody |  | Voltage Class : 400/ KV |  |  | Date Of Commission : 13-Feb-04 | [28 empty] | SSMD : Hoody |  | Voltage Class : 400/ KV |  |  | Date Of Commission : 27-Feb-96 | [26 empty] | SSMD : Hoody |  | Voltage Class : 400/220 KV |  |  | Date Of Commission : 31-Mar-95
Zone : BANGALORE |  | Make : ALSTOM |  |  | YOM : March-2012 | [9 empty] | Zone : BANGALORE |  | Make : ALSTOM |  |  | YOM : March 2012 | [6 empty] | Zone : BANGALORE |  | Make : GE T&D |  | YOM : 2017 |  |  |  | Zone : BANGALORE |  | Make : ALSTOM |  |  | YOM : May 2012 | [9 empty] | Zone : BANGALORE |  | Make : ALSTOM |  |  | YOM : May2012 | [5 empty] | Zone : BANGALORE |  | Make : ALSTOM |  |  | YOM : 2016 | [8 empty] | Zone : BANGALORE |  | Make : CGL |  |  | YOM : 2003 | [28 empty] | Zone : BANGALORE |  | Make : CGL |  |  | YOM : 1993 | [26 empty] | Zone : BANGALORE |  | Make : CGL |  |  | YOM : 1993
| Permissible limits as per IS 1866:2000 | [14 empty] | Permissible limits as per IS 1866:2000 | [11 empty] | Permissible limits as per IS 1866:2000 | [7 empty] | Permissible limits as per IS 1866:2000 | [14 empty] | Permissible limits as per IS 1866:2000 | [10 empty] | Permissible limits as per IS 1866:2000 | [13 empty] | Permissible limits as per IS 1866:2000 | [33 empty] | Permissible limits as per IS 1866:2000 | [31 empty] | Permissible limits as per IS 1866:2000
Last Filtn. Date |  | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | Permissible limits as per 1866-2017 | 2015 | 2015 | 2015 | 2015 | 2015 |  | Last Filtn. Date |  | 2015 | 2015 | 2015 | 2015 | Permissible limits as per 1866-2017 | 2015 | 2015 | 2015 | 2015 | 2015 | Last Filtn. Date |  | 2018 | Permissible limits as per 1866-2017 | 2018 | 2018 | 2018 | 2018 | Last Filtn. Date |  | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | Permissible limits as per 1866-2017 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | Last Filtn. Date |  | 2015 | 2015 | 2015 | 2015 | 2015 | Permissible limits as per 1866-2017 | 2015 | 2015 | 2015 | Last Filtn. Date |  | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | Permissible limits as per 1866-2017 | 2016 | 2016 | 2016 | 2016 | 2016 | Last Filtn. Date |  | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | Permissible limits as per 1866-2017 | 2016 | 2016 | 2016 | 2016 | Last Filtn. Date |  | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 1997 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | 2011 | Permissible limits as per 1866-2017 | 2011 | 2011 | 2011 | 2011 | Last Filtn. Date |  | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 1995 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | 2015 | Permissible limits as per 1866-2017 | 2015 | 2015 | 2015 | 2015
Sampling Date | [13 empty] | ` | Sampling Date | [11 empty] | Sampling Date | [7 empty] | Sampling Date | [14 empty] | Sampling Date | [10 empty] | Sampling Date | [13 empty] | Sampling Date | [33 empty] | Sampling Date | [31 empty] | Sampling Date
Date of Test | Permissible limits as per IS 1866:2000 | 2015-04-25 | 2015-04-27 | 2016-03-08 | 2017-04-20 | 2020-08-04 | 2021-01-12 | Vol Class Good Fair Poor | 2023-07-13 | 2023-01-20 | 2023-11-20 | 2024-10-30 | 2026-03-12 |  | Date of Test | Permissible limits as per IS 1866:2000 | 2015-04-27 | 2016-03-08 | 2017-04-20 | 2020-08-04 | Vol Class Good Fair Poor | 2021-07-13 | 2023-01-20 | 2023-11-18 | 2024-10-30 | 2026-03-12 | Date of Test | Permissible limits as per IS 1866:2000 | 2020-07-16 | Vol Class Good Fair Poor | 2023-01-24 | 2023-11-06 | 2024-10-03 | 2026-03-10 | Date of Test | Permissible limits as per IS 1866:2000 | 2015-04-27 | 2016-03-08 | 2016-10-20 | 2017-01-24 | 2017-04-20 | 2020-08-04 | Vol Class Good Fair Poor | 2021-01-12 | 2023-01-20 | 2023-11-18 | 2024-10-30 | 2025-02-13 | 2026-03-12 | Date of Test | Permissible limits as per IS 1866:2000 | 2015-07-15 | 2016-03-08 | 2017-04-20 | 2020-08-04 | 2020-12-09 | Vol Class Good Fair Poor | 2023-11-20 | 2024-10-30 | 2026-03-12 | Date of Test | Permissible limits as per IS 1866:2000 | 2016-10-17 | 2016-11-03 | 2016-11-08 | 2017-04-24 | 2017-12-16 | 2020-07-17 | Vol Class Good Fair Poor | 2022-01-07 | 2023-01-24 | 2023-11-06 | 2024-10-03 | 2026-03-10 | Date of Test | Permissible limits as per IS 1866:2000 | 2004-01-31 | 2004-06-01 | 2004-07-28 | 2005-02-14 | 2005-09-30 | 2006-05-08 | 2006-10-31 | 2008-02-12 | 2009-02-05 | 2009-08-05 | 2010-03-22 | 2010-11-03 | 2011-02-01 | 2011-05-16 | 2012-02-15 | 2012-05-08 | 2013-06-04 | 2013-07-31 | 2013-08-20 | 2014-05-31 | 2015-01-02 | 2016-06-08 | 2016-09-17 | 2016-09-23 | 2016-10-17 | 2017-04-24 | 2020-07-16 | Vol Class Good Fair Poor | 2023-01-24 | 2023-11-06 | 2024-10-03 | 2026-03-10 | Date of Test | Permissible limits as per IS 1866:2000 | 1997-10-03 | 2001-08-16 | 2001-11-26 | 2002-02-25 | 2003-04-05 | 2003-05-21 | 2004-06-01 | 2005-02-23 | 2005-09-27 | 2006-05-10 | 2008-02-11 | 2009-03-05 | 2009-04-08 | 2010-03-23 | 2010-09-22 | 2011-01-19 | 2011-05-16 | 2012-02-15 | 2012-05-08 | 2013-06-03 | 2014-05-31 | 2015-01-01 | 2016-06-08 | 2017-04-24 | 2020-07-14 | Vol Class Good Fair Poor | 2022-09-20 | 2023-11-06 | 2024-10-01 | 2026-03-09 | Date of Test | Permissible limits as per IS 1866:2000 | 2001-08-16 | 2002-02-25 | 2004-05-24 | 2004-06-02 | 2004-08-04 | 2005-02-28 | 2005-09-28 | 2005-11-19 | 2006-01-30 | 2006-05-10 | 2008-02-07 | 2009-01-24 | 2009-08-03 | 2010-03-20 | 2010-07-01 | 2010-11-04 | 2011-01-29 | 2011-05-17 | 2012-02-13 | 2012-05-08 | 2013-05-24 | 2013-12-04 | 2014-04-23 | 2014-10-07 | 2014-10-17 | 2015-01-05 | 2015-01-07 | 2015-01-22 | 2016-05-17 | 2017-04-24 | 2019-11-14 | 2020-07-13 | 2020-12-09 | Vol Class Good Fair Poor | 2022-09-20 | 2023-10-13 | 2024-09-30 | 2025-01-10
Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.0043 | 0.0139 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.058 | 0.0183 | 0.0077 | 0.0047 | - |  | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.01 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0251 | 0.0059 | 0.0157 | 0.0057 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.0086 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0267 | 0.0102 | 0.006 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0068 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0122 | 0.0188 | 0.011 | 0.0066 | 0.0087 | nil | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 | 0.05 | 0.003 | 0.0045 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0059 | 0.0098 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.05 |  | 0.05 | 0.0032 | 0.017 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0069 | 0.0055 | 0.015 | 0.0104 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.006 | 0.013 | 0.0069 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.0092 | 0.0095 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0176 | 0.0122 | 0.0179 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.05 | 0.2 | 0.1 | 0.05 | 0.05 | 0.016 | 0.05 | 0.05 | 0.05 | 0.3 | 0.06 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.0045 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0518 | 0.0198 | 0.0191 | - | Aci dity | 0.3 mg KOH / gm(Max) | 0.2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.06 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.017 | 0.0103 | 0.0265 | > 170kV < 0.1 0.1-0.15 >0.15 >72.5-170kV < 0.1 0.1-0.2 >0.2 <72.5kV <0.15 0.15-0.3 >0.3 | 0.0359 | 0.0288 | 0.0198 | 0.0179
Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 118.2 | 118.2 | 142.5 | 76.07 | 105.6 | 151.41 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 84 | 860 | 1250 | 904.4 | 354.4 |  | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 260.5 | 126.8 | 140 | 168.5 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 141 | 890 | 870 | 1300 | 1200 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 109.4 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 904.8 | 956 | 1200 | 1030 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 214.2 | 133.8 | 108.2 | 112.1 | 22.14 | 68.65 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 720.6 | 710 | 790 | 1400 | 1100 | 1000 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 151.2 | 212.9 | 167.3 | 241.4 | 235.68 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 890 | 2200 | 1300 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 79.54 | 176.8 | 31.02 | 161.2 | 139.4 | 156.2 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 1157 | 1310 | 1080 | 1200 | 1400 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 70.7 | 70.1 | 46.8 | 68.2 | 61.5 | 69.8 | 56.4 | 19.6 | 18.4 | 17.3 | 16.9 | 15.1 | 16.3 | 17.2 | 50.9 | 90.1 | 56.4 | 53.3 | 65.5 | 63.2 | 63 | 55.85 | 112.8 | 65.21 | 41.61 | 85.36 | 80.02 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 845 | 620 | 522.3 | 660 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 8 | 17.8 | 1.81 | 0.59 | 19.1 | 9.34 | 7.12 | 14.3 | 7.24 | 6.98 | 7.35 | 5.49 | 5.42 | 5.52 | 10.3 | 10.4 | 11.3 | 13.1 | 8.19 | 10.1 | 9.32 | 10.1 | 18.7 | 16.72 | 10.54 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 440 | 101 | 173.2 | 127.6 | Resis tivity | 0.1 X 10E 12 ohm-cm(Min) for all Class of voltages | 18.6 | 15.8 | 8.66 | 7.24 | 10.6 | 9.94 | 8.74 | 15.2 | 8.47 | 8.38 | 8.16 | 8.15 | 8.17 | 10.8 | 10.9 | 8.34 | 10.9 | 15.9 | 16.1 | 16.9 | 12.4 | 12.1 | 44.59 | 14.54 | 152.1 | 44.37 | 46.83 |  | 32.43 | 26.55 | 18.42 | 16.58 | 24.16 | > 170kV > 10 03-10 < 3 <170 kV >3 0.2-3 <0.2 | 48 | 260 | 101.9 | 180.2
Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0011 | 0.0011 | 0.00144 | 0.00054 | 0.00269 | 0.00148 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00047 | 0.000518 | 0.0025 | 0.00322 | 0.00207 |  | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.001 | 0.00111 | 0.00064 | 0.00103 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.001525 | 0.000537 | 0.000873 | 0.00081 | 0.00073 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00078 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00202 | 0.00215 | 0.00051 | 0.00895 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0008 | 0.00104 | 0.00055 | 0.00016 | 0.00129 | 0.00082 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.0018 | 0.000537 | 0.000943 | 0.000724 | 0.00051 | 0.00096 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0009 | 0.00089 | 0.00028 | 0.00254 | 0.00115 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.000809 | 0.000524 | 0.00077 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00058 | 0.00072 | 0.00162 | 0.0002 | 0.00069 | 0.00082 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.0002 | 0.000362 | 0.00086 | 0.000619 | 0.00455 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0001 | 0.0001 | 0.0005 | 0.0002 | 0.0002 | 0.0003 | 0.0018 | 0.0036 | 0.0033 | 0.0029 | 0.0031 | 0.0033 | 0.0027 | 0.0025 | 0.001 | 0.0006 | 0.0008 | 0.0008 | 0.0005 | 0.0006 | 0.0006 | 0.00044 | 0.00037 | 0.00055 | 0.00024 | 0.00041 | 0.00078 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.0025 | 0.00084 | 0.002 | 0.00583 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.00584 | 0.01 | 0.018 | 0.039 | 0.003 | 0.0046 | 0.0048 | 0.0038 | 0.0039 | 0.004 | 0.0045 | 0.0006 | 0.007 | 0.008 | 0.0031 | 0.0032 | 0.0029 | 0.0028 | 0.008 | 0.004 | 0.005 | 0.005 | 0.00544 | 0.00328 | 0.00461 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.00244 | 0.00397 | 0.00333 | 0.00323 | Tan - Delta | 0.2(Max) for 170KV & above 1.0(Max) for below 170KV | 0.0007 | 0.002 | 0.0032 | 0.0041 | 0.0024 | 0.0025 | 0.0036 | 0.0019 | 0.0038 | 0.0041 | 0.0014 | 0.0015 | 0.0013 | 0.0037 | 0.002 | 0.0016 | 0.0041 | 0.002 | 0.0023 | 0.003 | 0.003 | 0.0031 | 0.0022 | 0.0079 | 0.0034 | 0.0029 | 0.0024 |  | 0.00175 | 0.00149 | 0.00182 | 0.003 | 0.00408 | > 170kV < 0.1 0.1-0.2 >0.2 < 170 kV <0.1 0.1-0.5 >0.5 | 0.001489 | 0.00148 | 0.00183 | 0.00322
BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  |  | 56 | 85 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 79 | 86 | 89 | 67 | 91 |  | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  | 53 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 73 | 67 | 82 | 62 | 78 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 68 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 50 | 48 | 82 | 71 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [5 empty] | 92 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 69 | 82 | 75 | 45 | 65 | 56 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  | 56 | 66 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 80 | 74 | 91 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV |  |  |  | 85 |  | 69 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 84 | 60 | 65 | 96 | 88 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [5 empty] | 82 |  | 64 | 83 | 60 | 72 | 51 | 72 |  | 69 | 72 | 70 |  | 72 |  |  |  | 62 |  |  | 64 | 65 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 71 | 65 | 89 | 70 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | [9 empty] | 73 | 68 | 49 | 86 | 73 | 60 | 63 |  | 67 | 58 | 60 |  |  |  | 83 | 59 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 80 | 61 | 50 | 58 | BDV (T) | 50KV(Min) for 170KV & above, 40KV(Min) for voltages between 72.5KV & 170KV, 30KV(Min) for below 72.5KV | 2006-05-10: 80; 2008-02-07: 86; 2009-01-24: 52; 2009-08-03: 67; 2010-03-20: 68; 2010-07-01: 68; 2010-11-04: 54; 2011-01-29: 74; 2012-02-13: 74; 2012-05-08: 69; 2013-05-24: 55; 2015-01-05: 66; 2019-11-14: 71; 2020-07-13: 68; 2020-12-09: 62 | > 170kV >60 50-60 <50 >72.5-170kV > 50 40-50 <40 < 72.5kV >40 30-40 <30 | 86 | 65 | 61 | 45
BDV (B) |  | 59 | 59 | 90 | 97 | 53 | 81 |  | 72 | 80 | 88 | 52 | 88 |  | BDV (B) |  | 70 | 93 | 69 | 50 |  | 72 | 59 | 60 | 50 | 85 | BDV (B) |  | 60 |  | 80 | 53 | 80 | 82 | BDV (B) |  | 65 | 65 | 89 | 50 | 64 | 74 |  | 66 | 75 | 75 | 40 | 68 | 88 | BDV (B) |  | 64 | 63 | 76 | 43 | 59 |  | 68 | 64 | 88 | BDV (B) |  | 65 | 80 | 63 | 57 | 78 | 62 |  | 78 | 62 | 63 | 90 | 73 | BDV (B) |  | 71 | 78 | 50 | 70 | 60 | 52 | 69 | 52 | 60 | 56 | 72 | 50 | 63 | 52 | 62 | 70 | 43 | 82 | 63 | 64 | 63 | 64 | 47 | 80 | 77 | 58 | 59 |  | 54 | 67 | 85 | 69 | BDV (B) |  | 25 | 29 | 38 | 74 | 64 | 80 | 98 | 95 | 56 | 52 | 65 | 26 | 85 | 66 | 53 | 55 | 69 | 67 | 52 | 60 | 64 | 63 | 91 | 71 | 54 |  | 74 | 64 | 76 | 73 | BDV (B) |  | 12 | 82 | 82 | 77 | 81 | 69 | 50 | 60 | 74 | 69 | 50 | 50 | 65 | 64 | 67 | 50 | 56 | 74 | 66 | 63 | 26 | 61 | 76 | 44 | 45 | 62 | 70 | 65 | 53 | 64 | 69 | 63 | 56 |  | 81 | 60 | 76 | 41
IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 43 | 39.64 | 34.61 | >25 20-25 <20 (for all voltage class) | 34.21 | 35.79 | 34.6 | 36.51 | 36.89 |  | IFT | 15 Dynes / cm (Min) | 35 | 35 | 42 | 42.56 | >25 20-25 <20 (for all voltage class) | 37.1 | 36.18 | 34.89 | 38.03 | 38.65 | IFT | 15 Dynes / cm (Min) | 38.19 | >25 20-25 <20 (for all voltage class) | 32.82 | 38.89 | 33.95 | 36.93 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 40 | 37.81 | >25 20-25 <20 (for all voltage class) | 35.27 | 35.41 | 37.95 | 35.72 | 37.46 | 37.67 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 43 | 37.76 | 38.25 | >25 20-25 <20 (for all voltage class) | 35.79 | 37.4 | 38.03 | IFT | 15 Dynes / cm (Min) | 35 | 35 |  | 47.69 | 43.96 | 30.98 | >25 20-25 <20 (for all voltage class) | 34.9 | 35.92 | 38.73 | 36.1 | 36.31 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41.39 | 35.82 | >25 20-25 <20 (for all voltage class) | 29.15 | 36.1 | 37.48 | 26.29 | IFT | 15 Dynes / cm (Min) | 25 | 35 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 35.25 | 27.26 | >25 20-25 <20 (for all voltage class) | 27.28 | 28.72 | 30.06 | 30.83 | IFT | 15 Dynes / cm (Min) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 30 | 35 | 30 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36.77 | 34.79 | 28.19 | 28.84 | >25 20-25 <20 (for all voltage class) | 29.11 | 19.47 | 30.19 | 26.6
F P | 125° C (Min) | 165 | 165 | 170 | 162 | 174 | 165 | Max decrease 10% (for all class of Voltage) | 170 | 167 | 147 | 161 | 169 |  | F P | 125° C (Min) | 155 | 151 | 161 | 158 | Max decrease 10% (for all class of Voltage) | 158 | 158 | 168 | 172 | 164 | F P | 125° C (Min) | 170 | Max decrease 10% (for all class of Voltage) | 160 | 161 | 161 | 168 | F P | 125° C (Min) | 161 | 162 | 156 | 163 | 170 | 165 | Max decrease 10% (for all class of Voltage) | 168 | 164 | 159 | 168 | 156 | 167 | F P | 125° C (Min) | 155 | 151 | 161 | 166 | 160 | Max decrease 10% (for all class of Voltage) | 166 | 152 | 167 | F P | 125° C (Min) | 153 | 153 | 162 | 160 | 160 | 166 | Max decrease 10% (for all class of Voltage) | 169 | 159 | 169 | 163 | 162 | F P | 125° C (Min) | 155 |  |  | 155 | [5 empty] | 157 | 157 | 163 | 153 | 156 | 156 | 155 | 153 | 153 | 151 | 153 | 152 | 155 | 160 | 150 | 151 | 159 | 169 | Max decrease 10% (for all class of Voltage) | 168 | 164 | 170 | 159 | F P | 125° C (Min) |  |  |  |  | 148 | 146 |  | 146 |  |  |  |  | 149 | 149 | 155 | 155 | 156 | 161 | 159 | 157 | 156 | 157 | 147 | 156 | 159 | Max decrease 10% (for all class of Voltage) | 159 | 168 | 163 | 159 | F P | 125° C (Min) |  |  | 148 |  |  | 148 |  | 150 |  |  |  |  | 151 | 152 | 152 | 151 | 145 | 153 | 159 | 159 | 156 | 153 | 155 | 153 | 149 | 176 | 169 | 149 | 148 | 168 | 158 | 166 | 164 | Max decrease 10% (for all class of Voltage) | 160 | 167 | 167 | 154
ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 7 | 7 | 9 | 4 | 11 | 4 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 12 | 17 | 9 | 15 | 5 |  | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 9 | 9 | 9 | 7 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 13 | 20 | 18 | 4 | 6 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 6 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 13 | 21 | 11 | 7 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 10 | 5 | 1 | 6 | 8 | 4 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 14 | 19 | 13 | 26 | 7 | 5 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 9 | 8 | 10 | 22 | 14 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 14 | 18 | 7 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 2 | 7 | 10 | 7 | 5 | 8 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 9 | 20 | 10 | 7 | 5 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) | 19 | 11 | 14 | 14 | 10 | 6 | 12 | 14 | 5 | 12 | 8 | 9 | 11 | 7 | 9 | 2 | 28 | 7 | 8 | 10 | 11 | 14 | 6 | 10 | 4 | 7 | 12 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 16 | 20 | 11 | 6 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) |  |  |  |  | 12 | 11 | 12 | 9 | 7 | 10 | 10 | 18 | 10 | 7 | 8 | 9 | 19 | 10 | 20 | 11 | 20 | 15 | 14 | 14 | 24 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 16 | 18 | 30 | 12 | ppm | For 170KV & above - 20 PPM(Max) Below 170KV 40 PPM(Max) |  |  | 10 | 8 | 8 | 7 | 27 | 10 | 6 | 11 | 17 | 11 | 9 | 6 | 9 | 17 | 7 | 8 | 9 | 7 | 11 | 1 | 8 | 21 | 11 | 11 | 5 | 4 | 4 | 8 | 11 | 23 | 13 | > 170kV < 15 15-20 >20 >72.5-170kV < 20 20-30 >30 <72.5kV <30 30-40 >40 | 16 | 10 | 12 | 19
Remarks |  |  |  | Gases are within the limits.Tan Delta ,SFRA & IDAX tests may be got done. | [10 empty] | Remarks |  |  | Gases are within the limits.Tan Delta,SFRA & IDAX tests may be got done. | [8 empty] | Remarks | [7 empty] | Remarks |  |  | Gases are within the limits.Tan Delta,SFRA & IDAX tests may be got done. | [11 empty] | Remarks |  | Gases are within the permissible limits. | Gases are within the limits.Tan Delta,SFRA & IDAX tests may be got done. |  | Saampling error suspected. | [5 empty] | Remarks | [9 empty] | Due to equipment problem DGA test not conducted. |  |  |  | Remarks |  |  | Flash Point test is not carried out due to Equipment fault. Furnish Date of Commission. | Flash Point test is not carried out due to Equipment fault. |  | Flash Point test is not carriedout due to Equipment fault. |  | When compared with previous test reports there is variation in respect of value of item no 3. |  | Flash point test is not carried out due to equipment fault. | Furnish YOM & last date of filtration. |  |  |  |  | Compared to previous test result there is variation in respect of item 1,2 & 3. | When compared to previous test results there is large variation in respect of Resistivity & Tan Delta values. | Send oil sample again within one month. | [5 empty] | Send sample again within a month. | [5 empty] | Due to equipment problem DGA test not conducted. |  |  |  | Remarks | [5 empty] | When compared to previous test results there is large variation in respect of item no (2) & (3). As such send one more oil sample duly observing the sampling guidleines. |  | Flash Point test is not carried out due to Equipment fault. | When compared to previous test results there is variation in respect of Resistivity and Tan-Delta. | Flash Point test is not carriedout due to Equipment fault. |  |  | Filter the oil after the repair & send it for testing. See note 2. | Furnish YOM. |  | There is variation in respect of item no.2 &3. Clarify if the oil has been topped up already. | [15 empty] | Remarks |  | 2004-06-02: Flash point test is not carried out due to Equipment fault.; 2004-08-04: Flash point test is not carried out due to equipment fault.; 2005-09-28: Flash Point test is not carriedout due to Equipment fault. Send oil sample again as per the sampling guidelines enclosed; 2006-01-30: Flash point test & DGA test are not carriedout due to equipments fault.; 2009-01-24: Flash point test is not carried out due to equipment fault .; 2009-08-03: Furnish YOM & last date of filtration.; 2010-11-04: Though the gases are within permissible limits, it is trending. Hence send oil sample after a month.; 2013-05-24: Send oil sample again within one month.; 2014-04-23: When compared to previous test results there is variation in respect of Resistivity and Tan-Delta.; 2020-07-13: sampling error suspected.